## Slide 1
Photovoltaic Hosting Capacity of
Distribution Networks
March 2022
Matti Lehtonen

## Slide 2: Limiting factors of PV hosting capacity
Current capacity of transformers and lines
Voltage rise
Unbalance
  Negative sequence voltage
  Load current of neutral in LV
Flicker
Harmonics

## Slide 3
Voltage level
Std 50160: limits for 10 minute values
· 95% must be in the band Un +/- 10%
Measurement for one complete week
In addition, all the 10 min values must be between -15 .. +10 %
In LV-system, according to association of utilities (sener):
· good quality: 10 min values between 220…240 V
· normal quality: 10 min values between 207…244 V
· standard quality: 10 min values between 207…253 V
In MV-system, according to association of utilities (sener):
· good quality: 10 min values between Un +/- 4%
· normal quality: 10 min values between Un +/- 10%
· standard quality: 10 min values between Un +/- 10%
Voltage level is determined by voltage drop due to load current,
on-load tap-changer, off-load tap-changer and compensation.

## Slide 4
Impact of local generation on voltages
A
B
x
C
UA
UB
DU
U
x
Network voltage normally
UA
UB
DU
U
x
And if power generation in C
UC
For instance, VDE-AR-N 4105 gives 3% limit for voltage rise due to PV

## Slide 5
Voltage unsymmetry
Std 50160: limits for 10 minute values:
95% of the time the negative sequence component must
be less than 2% of the positive sequence component.
Unsymmetry is caused by:
· uneven loads between the three phases
· single-phase PV generation

## Slide 6: Voltage unsymmetry
Voltage negative sequence components reacts strong to single phase PV
If single phase batteries, situation easily gets even worse, better coordination needed
PV and BESS unsymmetry is superposed on natural negative sequence component caused by loads.
In 2018 a measurement campaign was done in Caruna & Helen networks for the existing background U2

## Slide 7: Load Unbalance Example
Measured data
Single household
VUmean ≈ 0.25 %

## Slide 8: Network models for PV HC
Three grids
Hosting Capacity (HC) w.r.t XFMR
Voltage boundaries
  ± 10%
  ± 5%
  -5/+3 %
Two cases:
  Three phase inverters
  Only single phase inverters
Predominantly Rural (PR)
Intermediate (IN)
Predominantly Urban (PU)

## Slide 9: Test Networks’ mean HCs and their limiting constraints with different voltage bands Rural (PR) – Suburban (IN)– Urban (PU) networks & Reference: MV/LV Transformer rating
 |  |  | Balanced (3-Phase) |  | Unbalanced (1-Phase) | 
Region |  |  | Limiting Constraint |  | Limiting Constraint | 
PR |  |  | E3 | 105.2661 | E4 | 24.7721
 |  |  | E3 | 54.1924 | E3-E4(both) | 24.7798
 |  |  | E3 | 35.6077 | E3 | 17.0346
 |  |  | E7 | 110.3156 | E4 | 58.0569
IN |  |  | E7 | 110.3075 | E4 | 58.0591
 |  |  | E7 | 110.3255 | E4,E3 | 58.0564
 |  |  | E7 | 107.8319 | E6,E4 | 40.7981
PU |  |  | E7 | 107.8106 | E6,E4 | 40.7950
 |  |  | E7 | 107.8090 | E3 | 37.8780
 |  |  | Balanced (3-Phase) |  | Unbalanced (1-Phase) | 
Region |  |  | Limiting Constraint |  | Limiting Constraint | 
PR |  |  | E3 | 105.2661 | E4 | 24.7721
 |  |  | E3 | 54.1924 | E3-E4(both) | 24.7798
 |  |  | E3 | 35.6077 | E3 | 17.0346
 |  |  | E7 | 110.3156 | E4 | 58.0569
IN |  |  | E7 | 110.3075 | E4 | 58.0591
 |  |  | E7 | 110.3255 | E4,E3 | 58.0564
 |  |  | E7 | 107.8319 | E6,E4 | 40.7981
PU |  |  | E7 | 107.8106 | E6,E4 | 40.7950
 |  |  | E7 | 107.8090 | E3 | 37.8780
E3: VOLTAGE RISE – E7:TRAFO CURRENT – E4:VOLTAGE UNBALANCE – E6: NEUTRAL WIRE CURRENT

## Slide 10
Fast voltage fluctuation (flicker)
Affects especially lighting and hence vision.
Also electronic equipment may be disturbed.
Fast voltage fluctuation is caused by,
· control of on-load tap-changer
· motor starting
· welding equipment
PV variation
Limits according to CENELEC:
Voltage %-change / Changes per minute

## Slide 11: Flicker limits
As defined by IEEE standard 1453-2004, flicker is the high frequency voltage variations that give rise to the noticeable illumination changes.
Normally characterized by:
  Short-term flicker () in time period of 10 minutes.
  Long-term flicker () in time period of two hours.
According to standard EN-50160, should be below 1 for 95% of the time during one week period.
German LV guide lines, VDE-AR-N 4105, make the criteria stricter; should be less than 0.5.

## Slide 12: PV and flicker
Irradiance varies according to the cloud cover
  Cloud enhancement factor (bending of light at edges) increases the output power over nominal
Inverter operation may cause additional flicker

## Slide 13: Simulation on flicker
Long term flicker at the end of a long LV line, half cloudy day
400V line, 1050m AXMK 4x70, transformer 50 kVA, 7 load nodes, PPV = 100 kVA, Pload = 50 kVA

## Slide 14: Harmonics…
Through Fourier series analysis, it is possible to decompose any form of periodic current into a series of simple sinusoids, which start at the power system fundamental frequency and occur at integer multiples (harmonics) of the fundamental frequency.
(Even harmonics are very rare in power systems)

## Slide 15: Origin of harmonic currents
Current harmonics are caused by non-linear loads such as rectifiers, thyristor drives, induction furnaces, etc. The current of these loads is distorted from the fundamental sinusoidal current waveform.
Current harmonics affect the system by loading the distribution system as the waveforms of the other frequencies use up capacity without contributing any power to the load. They also contribute to the losses in the system.

## Slide 16
Harmonic voltages
Std 50160: limits for 10 minute mean values.
total harmonic distortion THD 8% at maximum
Other harmonics:
Maximum allowed harmonics as % of the nominal voltage in LV-connection
point. Limits given up to the order 25.

## Slide 17
Maximum values for diode rectifiers
Harmonic order In/I1
5. 30%
7. 12%
11. 6%
13. 5%
Other sources of harmonics:
· discharge lamps
· power units of electronics
For PWM-inverters, like solar and EV
switching frequency ≥ 2kHz 
harmonics below 40 are minimal

## Slide 18
Harmonic parallel resonance
· More dangerous than series resonance
· Transformer load as harmonic current source
· Transformer inductance and capacitor in parallel
· Resistive load causes attenuation
· High risk of damage to the capacitor
Condition :
T
C
L
C
S
Y
Y
J
PV inverters may occasionally cause local resonances at higher frequencies

## Slide 19: Network models investigated for PV HC
Three grids
Hosting Capacity (HC) w.r.t XFMR
Voltage boundaries
  ± 10%
  ± 5%
  -5/+3 %
Two cases:
  Three phase inverters
  Only single phase inverters
Predominantly Rural (PR)
Intermediate (IN)
Predominantly Urban (PU)

## Slide 20
HC as Maximum PV Power
Per customer
HC as injected power per customer is compared to a common connection capacity of 17 kW (3x25 A).
Assuming that customers can export to the network as much as import without additional costs.
If all customers have PVs, then network HC is lower than 17 kW in all the regions, i.e. distribution network limits PV generation (Figure 9).
Customers could possibly demand for network reinforcement, unless DSO applies export limitation.
Figure 9: Hosting capacity as average injected PV power per customer

## Slide 21
HC as % of PVs among customers
Currently installed average PV plant power is 6 kWp [2] and 9.25 kWp [3].
Instead of varying PV power, this time the number of PV plants is increased.
Only a small portion of customers can install PVs at the current pace.
Voltage control can twofold the share in rural regions. However, the increase in urban networks is insignificant (Table 1).
If the trend continues, most of the customers will experience violations (Figure 10).
Table 1: Share of customers (%) with PV plants
Figure 10: Customers with power quality violations at four different shares of customers having 6 kWp PV plants

## Slide 22: Technical versus economical PV HC?
Economical hosting capacity and margin between technical and economical constraints [6]
Region | PVs (kW) | HC (%)
Rural | 5.4 | 87.0
Suburban | 21.2 | 84.8
Urban | 152.6 | 76.3
Economical hosting capacity

## Slide 23: Lessons learned
In urban and suburban networks, common limiting factor for PV HC is load current of secondary transformer or supply cable.
In rural and weak networks the voltage rise starts to dominate HC.
Occasionally flicker and harmonic resonances may cause local problems. Their levels will generally be increased due to PVs.
Due to unbalance, single phase PV generators have the potential of causing the limiting factor for PV hosting capacity in rural networks.
The limit due to unbalance in weak networks is due to negative sequence voltage, elsewhere due to overload of neutral wire