## Daily monitoring results
Please enter the daily process monitoring results here and the results from your group's post-treatment analysis on the Post-treatment results sheet
Day |  | Wed | Thu | Fri | Mon | Tue
Date |  | 2019-02-06 | 2019-02-07 | 2019-02-08 | 2019-02-11 | 2019-02-12
pH meter reading |  | 4.72 |  | 4.8 | 4.87 | 4.4
flow rate [ml/min] | Influent | 100 | 100 | 99 | 97 | 100
| PIX | 2.3 | 2.3 | 2.2 | 2.5 | 2.5
pH | Influent | 7.84 | 7.84 | 7.8 | 7.78 | 7.73
| After sedimentation | 4.28 | 5.07 | 5.28 | 6.25 | 5.77
| Effluent | 7.36 | 7.27 | 7.59 | 7.65 | 7.74
UV-254 absorbance | Influent | 0.452 | 1.777 | 1.936 | 0.46 | 0.448
| After sedimentation | 0.043 | 0.323 | 0.563 | 0.363 | 0.263
| Effluent | 0.048 | 0.395 | 0.669 | 0.341 | 0.288
Turbidity, NFU | Influent | 8.51 | 8.64 | 7.63 | 10 | 10.3
| After sedimentation | 2.48 | 5.39 | 6.9 | 10.5 | 9.62
| Effluent | 0.269 | 2.47 | 2.17 | 5.58 | 5.58
Fe concentration [μg/l] | Influent |  | 263.307 | 303.303
| After sedimentation |  | 1383.195 | 2033.13
| Effluent |  | 803.253 | 1309.9*
Alkalinity [mmol/l] | After sedimentation |  |  | 0.0436 |  | 0.808
X = (Vacid*Cacid)/ Vsample | Effluent |  |  | 0.4948 |  | 0.4692
*absorbance out of calibration curve range. Sample should have been diluted
Date | Notes: Record here the adjustments you made to the pilot, observations etc.
Wed 6.2.2019 | Sand filter was overflowing --> backwash. Sludge removed. Process seems to be working well. Flocs/solids are settling very well. Previous group had prepared new raw water with COD KMnO4 = 37.92 mg/l. Checking dosage mpix/mCOD = 0.96. This is little lower than from jar tests but well in the range 0.8-1.2 that gave good results
Thu 7.2.2019 | Ratio for mixers (rpm) was 81:33:12. Sandfilter level 25.6 cm. Backwasing of sand filter. Sandfilter level 18.5 cm after backwashing
Fri 8.2.2019 | 10 l of 1.51 g/l PIX prepared for the weekend. Sandfilter backwashed. Sludge removed 2x. pH set point increased to 5.2. pH after sedimentation had been a bit on the lower range of optimal for previous groups
Mon 11.2.2019 | Flocs are very small and not settling. There is not much sludge after the weekend. pH must bee too high (6.25 after sedimentation). pH set point was adjusted back down to 4.95. Sludge was removed. Filter did not need backwashing as not clogged due to low floc formation
Tue 12.2.2019 | Raw water tank almost empty. Water level ~5cm fom bottom. Flocs are very small looks similar as on monday, no visual change. PIX dose was increased to 2.9 ml/min and mixing speed reduced 50% from 10v to 5v. After 1 hour flocs look better but PIX dose has dropped back to 1.9 ml/min so it was increased again up to 3.4 ml/min