## Slide 1: ELEC-E8423 - Smart Grid Solar farms, their local grids and connection to the power system
Tomi Mäentausta
Sanna Häsä
17.03.2020
Unrestricted

## Slide 2: Introduction
Solar Farm:
Collection of solar panels on land or on water in order to generate electricity to feed into the grid.
Traditional commercial PV efficiency is around 20%, and with Concentrated systems around 30%.
Produced energy is highly depended on the geographical position
Areas of solar farms: 1,6*104 m2 1 MW crystalline solar panels without trackers
2,4*104 m2 1 MW thin film solar panels without trackers
“Solar farms, their local grids and connection to the power system”
Notes: On the left:
Solar belt of the globe determines the solar energy potential.
Source: World Solat Atlas
On the right:
Floating solar is more than doubled every year:
Cumulative installed capacity
2015: 65 MWp
2016: 132 MWp
2017: 585 MWp
2018: 1097 MWp
Source: Floating Solar Market Report 2018

## Slide 3: Installed PV capacity and future scenarios
Total installed PV power capacity grew by 25% to 509.3 GW by the end of 2018, up from 407 GW in 2017.
“Solar farms, their local grids and connection to the power system”
GLOBAL TOTAL SOLAR PV INSTALLED CAPACITY 2000-2018
Global Solar PV market scenarios:
600 GW in 2019, 900 GW in 2021 and 1.1 TW in 2022
Top 3 countries are China, India and US
WORLD TOTAL SOLAR PV MARKET SCENARIOS 2019-2023
Notes: On the left side:
Total installed PV power capacity grew by 25% to 509.3 GW by the end of 2018, up from 407 GW in 2017.
Although growth in the top 3 Asian markets slowed, the Asia-Pacific region further expanded its solar leadership in 2018, again representing more than half of the global power generation capacities.
Note that due to its large size, China is listed separately from the Asia-Pacific region).
Additions of 71.3 GW in 2018 resulted in 295.7 GW of total installed capacity, equal to a 58% global market share – a 3% points year-on-year growth.
The new growth phase of European solar pioneers couldn’t stop the continent from losing market share,which dropped by 3% points to 25%.
Still, Europe maintained its second position based on a cumulative PV capacity of 125.8 GW.
On the right side:
Top 3 global solar markets 2019. Next to China, we expect two other markets to add over 10 GW each this year. One will be India, which we expect
to become the second largest market this year, and the US, which will rank third.
Global solar market developments 2020 to 2023
Globally,In our Medium Scenario, we expect that total global installed PV generation capacity will pass the following milestones over the next 5 years: 600 GW in
2019, 900 GW in 2021 and 1.1 TW in 2022.
Source: SolarPower Europe: Global Market Outlook For Solar Power 2019 – 2023
https://www.solarpowereurope.org/wp-content/uploads/2019/09/20190510_SolarPower-Europe_Global-Market-Outlook-for-Solar-Power-2019-2023.pdf?cf_id=9254

## Slide 4: PV in the broader energy transition
In the past the share of PV in the global energy portfolio has been only 1% out of the 22% of the renewables in total.
In the scenario of 2050 the share of the PV is expected to increase significantly.
Future Trends in Solar:
1. Digital solar & storage in small and medium sized PV systems: Increased self-consumption rates for smart solar & storage prosumers
2. Large-scale solar & storage with grid intelligence: Flexilblity services to the grid.
3. BIPV – 3rd generation of Building Integrated PV is ready for the mass market
Notes: Source: SolarPower Europe / GLOBAL MARKET OUTLOOK FOR SOLAR POWER 2019-2023
On the Left:
Share of PV is 1% of all the produced energy
Share of renewables in total is 22% of all produced energy
On the right:
Future Trends in Solar:
1. DIGITAL SOLAR & STORAGE WHAT SOLAR PROSUMERS REALLY NEED
Increased self-consumption rates for smart solar & storage prosumers
Digital solar & storage are the base for any smart self-consumption model. While typical on-site solar systems can achieve a physical self-consumption rate of around 20 to 35%, smart solar & storage prosumers can even reach a 60 to 90% ratio.(Lightsource, Foresight, Good Energy, KPMG (2015): The Decentralised
Energy Transition)
Solar & storage microgrids
2. DIGITAL SOLAR & STORAGE II – UNLEASHING LARGE-SCALE SOLAR & STORAGE THROUGH GRID INTELLIGENT SOLAR
Thanks to smart controls, utility-scale solar plants can already provide flexibility services to the grid, allowing system operators to quickly adapt to changing
conditions. With the addition of storage, the potential of solar is fully tapped: solar energy can be dispatched at any time of the day, and has the capability to provide the same or better services and reliability than conventional power plants, because of fast and reliable regulation of active and reactive power, outlined in detail in
SolarPower Europe’s Grid Intelligent Solar report.
3. BIPV – THE NEXT GENERATION IS READY FOR THE MASS MARKET
Building integrated PV (BIPV)
The next-gen BIPV products are based on basically any solar cell technology available. While many use dominating crystalline silicon, there are also BIPV
products, such as solar roof tiles using naturally black CIGS thin-film technology. Some startups also develop lightweight and flexible organic PV solutions,
anticipating “connected and integrated buildings” (with smart lighting, smart windows, canopies in parks, shading infrastructures, agriculture-related buildings)
will fuel the growth of the global BIPV market.

## Slide 5: PV System options - Central or String inverters
“Solar farms, their local grids and connection to the power system”
Optimal solution depending on several factors: e.g
Size of the solar farm
Layout of the solar farm
Reliability / Redundancy requirements
Grid connection requirements
Also “hybrids” - string inverters combined together to work as a “central inverter” - existing
Notes: PV System
There is two main options to connect PV panels into the grid:
1) Either with one big central inverter (Modular, one module range 1MVA-5MVA; Sinacon PV - Siemens)
2) With several smaller string inverters (Total system size up to 6,3MVA; KACO inverters)
Benefit of Central Inverter:
Significant lower inverter cost
Faster installation
Benefit of String Inverters:
Higher Performance Ratio
Lower cost for DC wiring and combiner boxes
Shorter MTTR
Flexible installation without heavy machines

## Slide 6: Central Inverter PV System
1. PV DC connection:
Combiner Boxes
DC Fusing
DC-Cables to Inverter
2. MV Inverter Station:
Central-Inverter
MV transformer
RingMainUnit Switchgear
Skid or Container
4.&5. HV Grid Connection:
MV/HV Substation
HV Transformer
Switchboard Station
MV Switchgear
MV/AUX Transformer
7. Control Center
SCADA
Power Plant Control
Asset Management
Production Forecast
Tracker Control
(3&6 Additional energy system equipment like Battery Energy Storage System (BESS) and Power to Hydrogen production)
Notes: System structure with Central Inverter:
1. PV DC connection:
Combiner Boxes
DC Fusing
DC-Cables to Inverter
2. MV Inverter Station:
Central-Inverter
MV transformer
RingMainUnit Switchgear
Skid or Container
4.&5. HV Grid Connection:
MV/HV Substation
HV Transformer
Switchboard Station
MV Switchgear
MV/AUX Transformer
7. Control Center
SCADA
Power Plant Control
Asset Management
Production Forecast
Tracker Control
(3&6 Additional energy system equipment like Battery Energy Storage System (BESS) and Power to Hydrogen production)

## Slide 7: Grid Connected PV System
Inverters:
High efficiency
Input DC-voltage boost
Grid connection filter
Grid disconnection relay
DC switch
Maximum power point tracking control
  Inverters choose the best point of maximum voltage and current to produce maximum power from the solar cell module.
Anti-islanding protection
Grid synchronization
Data logging and energy metering
20 years or more lifetime
“Solar farms, their local grids and connection to the power system”
Small and intermediate systems (< 5 MW) are usually connected to the distribution system
Large systems (> 5 MW) are connected to the transmission system
Notes: Inverter is a core element of the solar system. The Inverter convert DC power into AC form and feed to the Electrical Grid.
A DC-DC converter is used to collect maximum DC power output from the solar modules at the solar radiation and temperature by including the Maximum Power Point Tracking Control. At the input terminal of the inverter by using the DC link capacitor constant voltage is maintained.
Couple main functions of the inverters in PV systems.

## Slide 8: Inverter technologies
1. Inverter efficiency for state-of-the art brand products 98% and higher
2. New semiconductor technologies (SiC or GaN) allow very high efficiencies and compact designs of string inverters, 1500 V maximum DC string voltage.
3. The market share of string inverters is estimated to be 52%. The market share of central inverters, is about 44%.
4. Central inverters tend to be cheaper than string inverters.
“Solar farms, their local grids and connection to the power system”
Notes: Most commonly used system are DC/AC inverters.
On the left:
String inverters can be connected to single PV arrays or combined as “hybrids” for the whole solar farms
On the right:
Central inverter, transformer and ring-main unit MV switchgear installed on the skid

## Slide 9: Effects of PV Grid connected systems on a Distribution network
Reverse power flow: Net Production > Net Demand.
Overvoltage along distribution feeder: Reverse power flow leads to overvoltage along distribution feeder.
Voltage fluctuation: PV power output changes due to irradiation dependency.
Voltage control difficulty: Due multiply supply point.
Power Losses: If plant is long distance from load.
EMI-issues: Due the high frequency converters.
Increased reactive power in grid: In PV system, inverters are openly operating at unity power factor to maximize active power generation. This reduce active power supply by the utility. However, reactive power is still same, thus, distribution transformer operate at low power factor and it reduces overall system efficiency.
PV-STATCOM functionality, reactive power feed into the grid during night time
“Solar farms, their local grids and connection to the power system”
Notes: Main issues on PV systems;
The voltage fluctuation caused by the change of PV power output can reach over 0.01pu, and the fluctuation of load rate can reach 40%.
STATCOM  PV-STATCOM=Static Synchronous Compensator. Through the power electronic processing STATCOM controls reactive power flow. Solar plants are used as STATCOM for increasing power transfer capacity.

## Slide 10: Conclusion
Global solar installation capacity is increasing. Developing techniques are emerging for PV cells and markets are growing rapidly, expected to be almost doubled by 2022
Two basic configurations of the solar farms are typically used, either string inverter or central inverter connected systems. Optimal solution depends on multiple factors.
Large scale PV farms together with Battery Energy Storage Systems can provide flexibility services to the grid. Also PV-STATCOM functionality feeding reactive power can be used.
“Solar farms, their local grids and connection to the power system”
Notes: Developing techniques and markets

## Slide 11: Source material used
Solar Power Europe, “Global Market Outlook for Solar Power 2019-2023” Available on: www.solarpowereurope.org
World Bank Group, ESMAP and SERIS. 2019. Where Sun Meets Water: Floating Solar Market Report. Washington, DC: World Bank.
World Bank Group, ESMAP and Solargis: Global Solar Atlas; https://globalsolaratlas.info/
KACO Inverters: https://kaco-newenergy.com/applications/inverters-and-systems-for-utility-scale-pv/
Photovoltaic eBoP solution: https://new.siemens.com/global/en/products/energy/medium-voltage/solutions/electrical-balance.html
V. Patel and J. J. Patel, "Power quality improvement of grid using solar photovoltaic farm," 2017 Innovations in Power and Advanced Computing Technologies (i-PACT), Vellore, 2017, pp. 1-6.
Rajiv K. Varma ,Ehsan M. Siavashi, Enhancement of Solar Farm Connectivity With Smart PV Inverter PV-STATCOM IEEE TRANSACTIONS ON SUSTAINABLE ENERGY, VOL. 10, NO. 3, JULY 2019
Fraunhofer ISE: Photovoltaics Report, updated: 14 November 2019. www.ise.fraunhofer.de
“Solar farms, their local grids and connection to the power system”