## Slide 1: ELEC-E8423 - Smart Grid PV hosting capacity of low voltage and medium voltage grids
Aleksi Ranta-aho
Väinö Valli
17.03.2020

## Slide 2: Introduction
In recent years, the installed PV capacity has increased rapidly in many countries due to government schemes aimed at reducing the CO2 emissions
PV integration reverses the normal power flow during high-generation low-loading period which can cause:
  Voltage rise
  Voltage unbalance (due to single-phase inverters)
  High currents (Thermal capacity of lines and transformers)
  Power quality problems (Flicker, Harmonics)
Hosting capacity (HC) is the limit how much PV power can be connected to distribution grid on a given location without any adverse impacts.

## Slide 3: PV hosting capacity of a feeder
Key factors determining the PV HC of a feeder:
  PV Location
    Smaller effect on voltage when PV is connected close to substation
  Feeder characteristics
    Larger conductor -> lower impedance -> Higher HC
  PV Control
    Power factor of the inverter output has impact on the voltage

## Slide 4: Restrictive operational limits
Incidence of the operational limit first violated by PV generation in
50,000 studied systems (most restrictive operational limit for PV
generation). (Torquato et al. 2018)
Overvoltage is the most significant limiting factor in > 60 % of the cases
Other restricting factors:
  Conductor thermal capacity
  Voltage unbalance
  Undervoltage
Notes: Voltage unbalance is defined as differences in voltage magnitudes or phase angles or both in a three phase system. It is caused by uneven distribution of loads between the three phases and single phase PV generation
Undervoltages occur in phases without PV generation when high PV power is injected into the other phases
Increasing the cable size reduces the overvoltage and the thermal capacity becomes the most limiting factor

## Slide 5: The key limiting factor - Voltage rise
Std 50160: limits for 10 minute values:
95% must be in the band Un +/- 10%
all the 10 min values must be between -15 .. +10 %
Notes: The Distribution System Operators (DSOs) are responsible for delivering power to all customers within the limits that are set in standards. The EN 50160 standard is used in Finland. The German LV standard VDE-AR-N 4105 is more strict as it gives 3% limit for voltage rise due to PV
For power to flow into the grid from the PV system, the voltage at the point of common coupling must be higher.
Figure on the left:
The figure illustrates how much difference there is in the per unit voltage in three different scenarios.
Figure on the right:
With PV systems connected to distribution grid, situations can arise simultaneously (and suddenly) where there is high consumption along one feeder (which leads to voltage drop) and high generation along another feeder (which leads to voltage rise).
This makes it challenging for the DSO to keep voltage within the limits for all customers.

## Slide 6: PV and flicker
The fluctuation of sun's irradiation causes flicker (fast changes in voltage)
  Flicker is also caused by inverters and MPPT-control
Flicker can be reduced by controlling the reactive power and in worst case curtailing the power production
Flicker can be experienced as fast changes in lighting illumination
  Even small illumination changes are harmful for humans
  Standard SFS-EN 50160 sets limits for flicker
Irradiance fluctuation (Arshad 2019)
Notes: Fluctuation of irradiation is caused by changes in the sky cloud cover. On a half cloudy day changes can be rapid.
In addition to variating PV production, flicker is caused by changes in the grid power (starting of large motors, welding equipment, on-load tap changers etc.)

## Slide 7: How to increase the hosting capacity
Restricting PV locations close to the substation
Network reinforcement
  Larger conductor sizes (lower impedances)
    Not cost effective but maximizes the HC
  Meshed operation of MV
    Leads to protection challenges
Transformers with On-load tap changer (OLTC)
  Showing great potential in HC enhancement
  Only used in primary substations so far (i.e. HV to MV)
Intelligent inverter control strategies
  Impacts of PV generation depend on system loading
    more PV generation can be allowed during high loading periods
  Active Power Curtailment (APC) & Reactive Power Control (RPC) of inverters
    Best results are obtained when both are utilized together with dynamic reference points
Battery energy storage systems (BESS)
  Power is not injected into the distribution grid and thus no impact on the grid
Notes: Meshed operation: Normally the distribution grids are operated in radial topology which is more simple to plan and operate than meshed topology. The meshed operation would reduce the impedance of the lines and thus reduce voltage rise. However, doing so only makes sense in urban areas and even then the more complex protection schemes might prove to be too expensive to implement.
Transformers with On-load tap changer (OLTC): On-load tap changer transformers can be controlled under load, which is useful in primary substation transformers (HV to MV) as we can regulate the voltage received by MV customers and secondary substations (MV to LV) without interruption to the supply. Typically, smaller and more common off-load tap changer transformers need to be deenergized before voltage can be adjusted. The secondary votlage can be adjusted 0.8-1.25% per step, up to maximum of +-15 % of the nominal voltage.
APC & RPC: PV inverters with advanced control algorithms are able to regulate the distribution grid voltages and reduce losses in the system. This results in increased hosting capacity.
In order to provide reactive power support, the inverter should be oversized respect to PV system’s rated AC output so it has the capacity to do so.

## Slide 8: Should PV be connected to MV or LV?
MV-connected PV quickly raises the voltage in its surrounding area leading to voltage problems in LV earlier than in MV
Largest installed PV capacity can be achieved by having most of the generation connected in LV rather than in MV
Need for integrated MV-LV models in future network planning
  Limiting the investigation only to a single voltage level might lead to misleading results
Notes: Figure: PV generation is happening purely on the MV-side. Even though no voltage problems occur on MV-side, LV busbar voltage crosses the saturatory limit.

## Slide 9: Conclusions
Hosting capacity is the limit how much PV power can be connected to distribution grid on a given location without any adverse impacts. Voltage rise is the most significant limiting factor of PV HC
Various techniques can be used to increase HC, facilitating the continued uptake of distributed renewable energy
Policies that aim to maximize the overall PV generation should encourage small scale PV units connected in LV rather than medium scale PV units connected to MV grid

## Slide 10: Source material used
R. Torquato, D. Salles, C. Oriente Pereira, P. C. M. Meira, and W. Freitas,“A Comprehensive Assessment of PV Hosting Capacity on Low-Voltage Distribution Systems,” IEEE Transactions on Power Delivery, 2018
A. Arshad, ”Voltage Control and Photovoltaic Hosting Capacity in Distribution Networks,” Doctoral dissertation, Aalto University, 2019
L. Collins and J. K. Ward, “Real and reactive power control of distributed PV inverters for overvoltage prevention and increased renewable generation hosting capacity,” Renewable Energy, 2015
M. Davoudi, V. Cecchi, and J. R. Agüero, “Effects of stiffness factor on bus voltage variations in the presence of intermittent distributed generation,” in 2015 North American Power Symposium (NAPS), 2015
A. Ballanti and L. F. Ochoa, “On the integrated PV hosting capacity of MV and LV distribution networks,” in 2015 IEEE PES Innovative Smart Grid Technologies Latin America (ISGT LATAM), 2015
S.M. Ismael, S.H.E. Abdel Aleem, A.Y. Abdelaziz, A.F. Zobaa, “State-of-the-art of hosting capacity in modern power systems with distributed generation”, in Renewable Energy, 2019
M. Lehtonen, “Photovoltaic Hosting Capacity of Distribution Networks (PP slides)”, 2019