## Slide 1
ELEC-E8423 - Smart Grid Active Voltage Control in Smart Grid
Oula Lehtinen​
Atte Weckman
09.04.2019
Page 1 / 11

## Slide 2
Introduction: General aspects of voltage in distribution networks
Emerging problems due to increasing amount of distributed generation (DG)
Methods for controlling the voltage: passive and active
Voltage control architectures (VCAs)
Different time scales of active voltage control (AVC)
Barriers and challenges for AVC in current systems
Conclusions
Contents
Active voltage control in SG
09.04.2019
Page 2 / 11

## Slide 3
Voltage quality
Voltage quality standards in distribution networks: EN 50160 sets the minimum requirements, but DNOs often apply stricter limits
EN 50160: Voltage level deviations Un,rms ± 10 %, 95 % of the time, 10-minute periods
Voltage quality covers also rapid voltage changes (flicker), voltage dips, interruptions, phase unbalance and harmonics
Voltage drop
Especially in rural areas with long OHL feeders, capacity of the grid is limited by voltage drop
Function of R, X, P and Q
If the voltages are near their nominal value and the angle between voltage phasors is small, voltage drop can be approximated using only the longitudinal component
In MV networks, R and X are usually of the same magnitude. Thus, both real and reactive power flows affect network voltages
Introduction:
General aspect of voltage in distribution networks
Active voltage control in SG
09.04.2019
Page 3 / 11
From [1]
From [1]

## Slide 4
Traditionally, planning of MV and LV grids has been based on max. demand / min. production & min. demand / max. production
DG almost always increases the voltage level in the network because the generated real power is usually significantly larger than the possibly consumed reactive power
In weak networks, hosting capacity for DG is often limited by the voltage rise effect
Flicker due to intermittency of renewable energy sources (RES) like photovoltaics (PV)
Motivation for AVC is to increase the hosting capacity of distribution networks for DG while maintaining reasonable connection costs
Emerging problems due to increasing amount of distributed generation (DG)
Active voltage control in SG
09.04.2019
Page 4 / 11
Adapted from [1]

## Slide 5
Methods for controlling the voltage:
passive and active
09.04.2019
Page 5 / 11
Active voltage control in SG
Passive methods ("Passive" - no way of controlling)
Grid impedance: stronger lines (increased conductor size) and/or shunt capacitors
MV/LV transformers may have fixed off-circuit taps
Connecting DG on a dedicated feeder
Active methods ("Active" - operation based on network's state)
On-load tap-changers (OLTCs) at the primary substation HV/MV transformers
Grid-tied inverters (GTIs) used along DG can support the voltage by
  Reactive power control (RPC) (Q(V) droop control)
  Active power curtailment (APC)
Line voltage regulators (LVRs): active voltage regulation anywhere along the line by feeder transformer
Static VAR compensators (SVCs): continuous VAR support by thyristor-controlled reactors (TCRs), capacitor banks and/or inductors
Static synchronous compensators (STATCOMs): Voltage-source converters, inject grid supporting voltages to the grid
Distributed energy resources (DERs), e.g. controllable loads, EVs, energy storages
From [2]
From [3]

## Slide 6
Voltage control architectures (VCAs)
09.04.2019
Page 6 / 11
Active voltage control in SG
Distributed / Local Voltage Control (LVC)
  At the point of DG integration
  The simplest approach, minimum data needed, least computational time, no communication needed
  Mitigating both fast and slow voltage deviations
  RPC using Q(V) droop control, APC, possibly DERs
Centralized / Coordinated voltage control (CVC)
  Number of controllable components vary
  Strong communication infrastructure often needed
  State-estimation, load-forecasting and sophisticated optimization tools like (non-)linear programming, metaheuristics (genetic algorithms, particle swarms), neural networks etc.
  Often computationally costly, tend to become slow
Hybrid: combination of LVC & CVC
  Multilevel VCA, e.g. combination of local flicker control, local voltage deviation control and higher-level coordination of GTI droops, DERs and substation OLTC
From [2]
From [2]

## Slide 7
A voltage control architecture (VCA) for high PV penetration, introduced in [2]:
Different time scales of active voltage control (AVC)
09.04.2019
Page 7 / 11
Active voltage control in SG
Method | Operation cycle | Goal | How? | Communication needs
Fast LVC | 100 ms | Mitigate flicker instantaneously (due to irradiation variation caused by cloud movement). Keep voltage at the same level as at the last step. | Inverters (GTI): RPC during low production RPC & APC during high production | Local measurements only
Slow LVC | 1 s | Mitigate voltage level deviations. Keep node voltage at 1 p.u. (within the dead band). | Inverters (GTI): RPC & APC droop control | Local measurements only
Slow CVC | 1 min | Reduce violations using coordinated control. Keep node voltages at 1 p.u. (within the dead band) and avoid APC. | Utilize full potential of Q-support of all GTIs, Accept APC as the last option. | Data share between PV nodes and primary substation control agent
Results from simulations [2]:
 | Voltage deviation (%) | Active power curtailed | Max. Flicker index at the weakest node
No control | 8.59 | 0 MW | ~ 45 %
Fast LVC (flicker control) | 10.05 | 11.6291 MW | ~ 13 %
Full hybrid control (LVC+CVC) | 2.0584 | 0.0211 MW | ~ 19 %

## Slide 8
The number of real world AVC implementations is still low due to following reasons:
AVC radically changes the operational and planning principles of distribution networks; DNOs should trust the control capability of privately-owned resources
Majority of AVC research is academically oriented and it focuses on control principles, not that much on the real-life implementations
Currently, network planning tools are not capable of taking AVC into account. The planning procedures need to be developed to enable comparison of the total costs of alternative voltage control strategies
The current regulative environment in Finland does not provide additional value to the network for grid automation. Therefore, there is no economic incentive that promotes grid automation in comparison to stronger connections
Some active voltage control methods require information on the state of the whole distribution network which is not, at present, usually available. However, AMRs could provide more data in the future
Barriers and challenges for AVC in current systems
09.04.2019
Page 8 / 11
Active voltage control in SG

## Slide 9
Coordinated voltage control (CVC) yields better results than local voltage control (LVC) alone, but needs more computation and communication infrastructure
Some active power curtailment (APC) is inevitable with high PV penetration in order to meet the voltage standards (without DERs)
Integration of AVC should be integrated to planning procedures and control software (SCADA, DMS) of DNOs and regulation should somehow encourage DNOs to make smart investments
Conclusions
09.04.2019
Page 9 / 11
Active voltage control in SG

## Slide 10
[1] Kulmala, A. Active Voltage Control in Distribution Networks Including Distributed Energy Resources. Tampere University of Technology. 2014. [2] Arshad, A & Lehtonen, M. A comprehensive voltage control strategy with voltage flicker compensation for highly PV penetrated distribution networks. Electric Power Systems Research, Volume 172, Pages 105-113. 2019.
[3] Hussein, M & Mahmoud, K. Combined Static VAR Compensator and PV-Inverter for Regulating Voltage in Distribution Systems. Nineteenth International Middle East Power Systems Conference (MEPCON), Egypt, 19-21 December 2017. [4] Kulmala, A., Repo, S., & Järventausta, P. Increasing penetration of distributed generation in existing distribution networks using coordinated voltage control. International Journal of Distributed Energy Resources, (5), 227-255. 2009. [5] Carlen, M. et al. Line voltage regulator for voltage adjustment in MV-grids. Cired, 23rd International Conference on Electricity Distribution, Lyon, 15-18 June 2015.
Source material used
Page 10 / 11
Active voltage control in SG
09.04.2019

## Slide 11
Questions or comments?
Page 11 / 11
Active voltage control in SG
09.04.2019