## Slide 1: ELEC-E8423 - Smart Grid Wind farms, their local grid and connection to the power system
Ilkka Jokinen
Taavi Heikkinen
19.03.2019

## Slide 2: Introduction
Overall structure of wind farm
Local grid
Connection to power system
Requirements of connection

## Slide 3: Wind farms in Finland
Wind production in Finland: 5,9 GWh (6,8%)
134 operating wind farms
Largest 117 MW, 34 wind turbines in Kristiinankaupunki
Completion of new project takes 4-6 years
  Grid connection
  Environmental impact
  Permits
No new installed capacity in 2018
Picture: https://ethawind.com/map/

## Slide 4: Structure of a wind farm
Distance between turbines
  Downwind 3-5 x rotor diameter
  Crosswind 5-10 x rotor diameter
  Energy loss ~ 2-5 %
Topology of electric grid
Capital costs (onshore)
  Turbines 65-85 %
  Local grid and connection 10-15 %
  Construction 5-15 %
Manwell et al., 2009
Smail et al., 2017

## Slide 5: Local grid
Wind generator output 650-690 V
Step-up transformer in the tower LV/MV
Each group of turbines connected to the MV/HV substation by MV network
~ 20 MW plant can be connected to substation with other radial connections
~ 100 MW plant, only connection
Most existing plants in Finland < 25 MW
https://www.wind-energy-the-facts.org/electrical-system.html

## Slide 6: A methodology for compatibility evaluation of wind generation integration in power systems
The continuous increase of the rate of power of single turbines and the particular generation condition of wind turbines makes evaluation of the compatibility of wind generators and the power systems necessary
Four factors may be taken in account:
  Electrical power system characteristics
  Wind turbine technology
  Grid connection requirements
  Simulation tools
1. General grid code requirements
2. Special requirements for wind generation
Source: Wind Turbine in Power Systems and Grid Connection requirements.
A. Sudria, M. Chindris, A. Sumper, G. Gross, F. Ferrer
Notes: Electrical power system characteristics
The characteristic of the power system, where the wind generation is connected to, influences highly the impact on system power quality. System voltage, short circuit power, line impedances are some of the most important characteristics that limit the network capability to admit wind power generation.
B. Wind turbine technology
The impact of wind generation in power systems depends on the used technology, the structure of the internal distribution network in the park, the control mechanism of each wind turbine and the overall control of the wind farm. All these factors should be known in order to analyze the impact on the power quality parameters at the connected grid.
C. Operation limits through grid connection requirements
In order to evaluate the impact of a wind generation to its connected power system network, grid connection requirements and limits for power quality impact are established. The objective is to fix limits in which an operation of wind generation is considered safe for system operators. If these limits are exceeded, it means that in some circumstances the power system can become instable and other connection strategies should
considered.
D. Simulation tool
In order to evaluate the impact of a wind generation to its connected power system network, grid connection requirements and limits for power quality impact are established. The objective is to fix limits in which an operation of wind generation is considered safe for system operators. If these limits are exceeded, it means that in some circumstances the power system can become instable and other connection strategies should
considered
D. Simulation tool
Once operations limits have been defined, the impact has to be analyzed by suitable simulation tools. The most complex task in this step is accurate modeling of the
wind farm.

## Slide 7: Impacts on the Transmission Grid
The connection of wind generation to electrical power systems influences:
  Voltage variation of amplitude and frequency
    Rise or variation around the nominal value compared to case without wind power production
  The load flow of real and reactive power
    Induction generators usually consume reactive power, which have to be compensated
      If the wind turbine units are double fed asynchronous generator or full converter generator, reactive power is controllable
  Power losses
    Depending on the location of production and consumption, wind power can increase transmission losses (in case of wind farms)
  Flicker
    Rapid fluctuation of the voltage level
  Harmonics
    Non linearities in the source may produce harmonics
  Short circuit currents and protection systems
  Stability

## Slide 8: Because of these, Grid Connection Requirements are needed
Grid connection requirements can be divided into two categories:
  General grid code requirements
    Represents requirements for every generator in the grid
    These are general requirements regarding the system operation point
    Some of the most important requirements are:
      Steady state voltage variation
      Line capacity
      Short circuit power at the connection point
      Frequency variations
      Protection
      Contingency
  Special requirements for wind generation
    Special requirements for wind generation were introduced to insert wind power generation in the power system without an impact on power quality or system stability
    Two differenf types of requirements:
      Requirements established by system operators
      National or internationaö standards
Notes: Active power control is required in order to limit overproduction of wind power that can lead to
instabilities due to island conditions
Frequency in the power system is an indicator of the balance between production and consumption.
The control of reactive power at the generators is used in order to keep the voltage within the required limits and
avoid voltage stability problems. Wind generation should also contribute to voltage regulation in the system; the requirements either concern a certain voltage range that should be maintained at the point of connection or certain reactive power compensation that should be provided.
Due to the high penetration of wind generation, system operators observe a certain risk for the system stability during major disconnections. Therefore, in the new regulations require that wind farms stay connected during a line voltage fault and participate in recovery from the fault.
National and international standards are applied to wind power generation regarding power quality issues for the emission of disturbances in the power system by wind generators.

## Slide 9: Requirements in case of Denmark
Active power
Possible to reduce power to less than 20% of nominal power within less than 2 seconds
During a transient fault situation, the full power must halt and a subsequent power increase must be possible within approximately 30
seconds
Frequency
Frequency operation is allowed between 49 and 50.3 Hz and beyond the outer limits of 47 and 53 Hz
the turbines have to disconnect within 300 ms
Reactive Power
Wind farms are required at the grid connection point to provide reactive power at any
operating point (PF=1).
Depending on the system voltage, voltage reduction can be require
Fault ride through
Wind farms have to stay connected and stable under permanent 3-phase faults and transient
2-phase fault, on any arbitrary line.
The wind farm must be controllable for up to 3 faults within 2 minutes or up to 6 faults if the delay between the faults is 5 minutes.
Eltra
Notes: Eltra is the transmission system operator in Western Denmark

## Slide 10: Conclution
Wind farms connected to HV grid by local MV grid
Impacts to the power systems
  The penetration of wind power increases exponentially and because of that it can cause large effects on power quality
Requirements
  Requires requlations

## Slide 11: Sources
A. Sudria, M. Chindris, A. Sumper, G. Gross & F. Ferrer ― Wind Turbine Operation in Power Systems and Grid Connection Requirements, Electrical Power System Department, March 2005. Available: http://www.icrepq.com/full-paper-icrep/309-SUMPER.pdf
P. Sorensen ― Grid connection of wind, available: lbrpowerhttps://www.coursera.org/lecture/wind-energy/grid-connection-of-wind-power-luqDg
S. Uski ― Wind Power Grid Connection, Ampner, October 2018
Ethawind 2019, Suomen tuulivoimapuistot.Available: https://ethawind.com/fi/info/
J. Mannwell, J. Mcgonowan & A. Rogers. Wind energy explaned, 2009. Available:http://ee.tlu.edu.vn/Portals/0/2018/NLG/Sach_Tieng_Anh.pdf
S. Krohn, P. Morthorst & S. Awerbuch. The Economics of Wind Energy, 2009. European Wind Energy Association. Available: http://www.ewea.org/fileadmin/files/library/publications/reports/Economics_of_Wind_Energy.pdf
H. Smail, R. Alkama & A. Medjdoub, Optimal design of the electric connection of a wind farm. https://doi.org/10.1016/j.energy.2018.10.015
Suomen tuulivoimayhdistys, 2019. Tietoa tuulivoimasta. Avalable: https://www.tuulivoimayhdistys.fi/tietoa-tuulivoimasta/tietoa-tuulivoimasta