## Slide 1: ELEC-E8423 - Smart Grid PV hosting capacity of low voltage and medium voltage grids
Jakov Chavez Vega
Kalle Valtavirta
5.3.2019

## Slide 2: Introduction
  Renewable energy sources covers 85% of global electricity production in 2050
  Increasing amount of PV in electricity production creates problems in LV and MV network
    Voltage rise
    Thermal
    Unbalance of systems
    Loading constraints exceeds
  How hosting capacity can be increased?
Notes: Increasing amount of PV in electricity production creates problems in low and medium voltage grids.
Voltage rise
Thermal
Unbalance of the system. The amount of single phase solar inverters increases when moving towards the concept where consumers becomes producers. In case of connecting many single phase inverters to the grid without further studies, the voltage balance may break. When three phase system lost its symmetry, connected devices may be disturbed and losses are increasing.
Loading constraints exceeds such as cable ampacity and transformer ratings.
So in general, the grid cannot tolerate effusive amount of distributed PV production and this characteristic is called the PV hosting capacity of the grid. The hosting capacity can be still increased.

## Slide 3: Factors determining PV hosting capacity
  Main factors determining the PV hosting capacity of feeder
    Size of PV
    Location
    Feeder characteristics
    Electrical proximity to other PV
    PV control
  Load does not determine the hosting capacity
Notes: First before looking solutions for increasing the hosting capacity, we need to know what factors determines the PV hosting capacity.
The main factors determining the PV hosting capacity of feeder are:
Size of the PV power plant.
Location. If the PV is integrated to the grid close to the substation, it has smaller effect to voltage rise compared to the PV far from station.
Feeder characteristics such as voltage sensitiveness and short circuit capabilities. Like said earlier, loading constraints exceeding. By upgrading the cables and transformers, the hosting capacity may increase but this may not be the best way to do this.
Electrical proximity to other PV. If much PV are integrated to the same feeder, every PV plant makes voltage to rise. Every PV plant also has unique variable production which why the hosting capacity changes in real time.
PV control. How much the PV plants are limited at the time.
By looking the actual load does not provide everything information to us determining the PV hosting capacity

## Slide 4
Some of the key characteristics of 15 different test feeders
0
Notes: A total of 5000 PV scenarios with various PV penetrations are studied to obtain the hosting capacity.
The penetration of PVs spread from 2 % to 100 %.
feeder-12 has the largest kVAR support from the capacitors

## Slide 5: Technologies to increase PV hosting capacity
  PV locations
  PV power factors
    Unified constant power factor
    Volt/VAR control
  Simulations
  Increasing the ampacity of cables and rating of transformer
Notes: Here are couple technologies how the PV hosting capacity can be increased.
PV hosting capacity can be increased by restricting PV locations closer to the substation. PV locations based on the primary impedance has better performance than restricting PV locations based on the feeder length.
PV hosting capacity can be increased by producing reactive power to the feeder. This is usually done by controlling the power factor of solar inverter. By producing reactive power to the grid, we can control the voltage rise and drops in the feeder.
Simulations of the voltage rise and heating of the cables can be performed and different scenarios can be considered.
The most simple solution to increase the hosting capacity of the feeder is to replace old cables with cables that have higher ampacity limit and with transformers that have higher ratings. Still this is not the best solutions because of the intermittent production of PV. Cables and transformers with higher constraints are more expensive and most of the time cables and transformers are too good for the feeder.

## Slide 6: Advanced techniques
  Feeder reconfiguration
    Changes distances and impedances of all PV locations
  PV power factor (pf) setting
    A smaller leading pf  more reactive power into the feeder
     pf should be optimized for each PV
  Volt/var optimization
    PV inverters consume reactive power to avoid overvoltage
    At the same time causing voltage deviation in the system
     Compromise between overvoltage and voltage deviation
  Generic optimization problem formulation
Notes: Feeder reconfiguration. In addition to increasing the ampacity of the cables, the feeder cable topology can also be reconfigured, which in turn changes the distances and impedances of all PV locations. Feeder reconfiguration is generally used to reduce energy losses and improve voltages, but with DG, feeder reconfiguration can be used to improve the HC. Simulations have to be run with the objective of maximizing the DG power in the feeder. The reconfiguration can be done during the planning stage of the project or during the project with the use of remotely operated switches. However a sufficient amount of remote switches is needed.
PV power factor setting. The PV power factor affects the HC greatly. A smaller leading PF will usually cause more generated reactive power into the feeder. For optimal operation, the PF should be optimized for each PV to have its unique PF. Furthermore with the ability to control the PF of a PV, it would be possible to increase the HC.
Volt/var optimization. Most PV inverters are consuming reactive power from the feeder so that the overvoltage problem could be avoided. This however causes voltage deviation in the system. In order to compromise between the overvoltage and voltage deviation, volt/var optimization can be utilized. Volt/VAR is used to manage voltage levels and reactive power to achieve more efficient gird operation by reducing system losses, peak demand or energy consumption or a combination of the three. Different volt/var functions will provide different VAR support.
Generic optimization problem formulation. The above cases are all optimization problems with different constraints (power flow, voltage limits, thermal limits, topology limits, PV limits) and other user-defined limits. They can be solved with different kinds of algorithms.

## Slide 7: Other techniques
  Battery energy storage system (BESS)
    Demand is smoothened out by shaving demand peaks
    Prices of batteries will drop in the future
    Electric vehicles
  Voltage control using on-load tap changer (OLTC) of a transformer
    Stepped voltage regulation
    Automatic compensation for the voltage profile of the network
  Active power curtailment of PV output
    Distributed system operators ask DGs to decrease their output
    Useful in centralized DGs
  Common grid codes
Notes: BESS. Allows the the demand and generation to be smoothened out by shaving of the demand peaks. Regenerating during high production and injecting during high demand. However with 1-phase BESS, it’s important to install the BESS and the PV on the same phase to increase the HC. If the phases are randomly selected, the HC actually reduces. 3-phase BESS are more expensive, but have a lower impact on the power quality. In the future, when prices of batteries will decrease. EVs is a big possibility.
OLTC. Allows stepped voltage regulation of the output of transformers. OLTCs provide automatic compensation for the voltage profile of the network, which in turn increases the HC.
Active power curtailment. DSOs can ask DGs to decrease their output power to match consumption requirements in order to maintain the operation limits of the grid. Useful in centralized DGs, when the DSOs can access DG stations and control their output power.
Common grid codes. that set restrictions on new PV installations.

## Slide 8: Conclusions
  PV hosting capacity is the total PV power that can be accommodated on a given feeder without any adverse impacts
  Factors such as size of PV, location, feeder characteristics and PV control determine PV hosting capacity
  PV hosting capacity can be increased by several different techniques

## Slide 9: Some techniques to increase hosting capacity

## Slide 10: Source material used
Smith, J. & Rylander, M., PV Hosting Capacity on Distribution Feeders, Electric Power Research Institute, IEEE PES Washington, D.C, 2014.
Fei Ding, Barry Mather, and Peter Gotseff, National Renewable Energy Laboratory (NREL), Technologies to increase PV hosting capacity in Distribution Feeders, IEEE, 2016.
Green, J; Roark J; Parks J, Determining the impacts of volt/VAR optimization: a tale of two approaches, Electric Light & Power and POWERGRID International, 2015.
Arshad, A; Püvi, V; Lehtonen, M, Monte Carlo-Based Comprehensive Assessment of PV Hosting Capacity and Energy Storage Impact in Realistic Finnish Low-Voltage Networks, MDPI Energies, 2018.