## Slide 1: ELEC-E8423 - Smart Grid Frequency Containment and Frequency Restoration Reserves in Nordic Power System
Svetlana Rybina, Lauri Holopainen
19.03.2019

## Slide 2: Introduction
+ Frequency is one of the important parameters of power quality (should stay f=50 Hz all the time)
+ Electricity production = Electricity consumption
+ Main supply/demand balancing is made on financial, day-ahead (Elspot) and intra-day (Elbas) markets before actual energy use
+ Not possible to make absolutely exact forecast  real time balancing required
Balancing capacity markets
(frequency reserve markets)

## Slide 3: Nordic Model
+ Joint Nordic agreement (Finland, Sweden, Norway and East Denmark) of TSOs (Transmission System Operators) to to sustain power quality at all times
+ Balancing capacity (balancing frequency) markets are maintained by national TSOs within own country
+ Some resources are purchased from neighboring countries (max 1/3 of frequency containment can be bought from other Nordic countries )
+ Finnish TSO is Fingrid

## Slide 4: Nordic Frequency Balancing Market structure
FCR-N: constantly maintained for frequency regulation of the normal state (~3 min)
FCR-D: for withstanding disturbances without frequency deviation more than 0,5 Hz
aFRR: automatically activated reserve meant to manage with continuous shifts (~2 min)
mFRR: activated by request within 15 min
Some power systems are utilizing secondary markets for reserves or RR (replacement reserve)

## Slide 5: Technical requirements
 | Minimum size | Full activation time
FCR-N | 0,1 MW | in 3 min after frequency step change of ± 0,1 Hz
FCR-D, power plants | 1 MW | 5 s / 50 % 30 s / 100 %, after frequency step change of -0,50 Hz
FCR-D, relay connected | 1 MW | Option 1: linear regulation 5 s / 50 % 30 s / 100 %, after frequency step change of -0,50 Hz Option 2: immediate disconnection when frequency 5 s ≤ 49,7 Hz OR 3 s ≤ 49,6 Hz OR 1 s ≤ 49,5 Hz immediate disconnection when frequency 5 s ≤ 49,7 Hz OR 3 s ≤ 49,6 Hz OR 1 s ≤ 49,5 Hz

## Slide 6: System frequency
The electric frequency in the network (the SYSTEM FREQUENCY f) is a measure for the rotation speed of the synchronised generators. By increase in the total DEMAND the SYSTEM FREQUENCY (speed of generators) will decrease, and by decrease in the DEMAND the SYSTEM FREQUENCY will increase
Regulating units will then perform automatic PRIMARY CONTROL action and the balance between demand and generation will be re-established
The FREQUENCY DEVIATION is influenced by both the total inertia in the system, and the speed of PRIMARY CONTROL
Under undisturbed conditions, the SYSTEM FREQUENCY must be maintained within strict limits

## Slide 8: Smart Grids in frequency control
Controlling the charging would make it possible for the EVs to minimise their energy costs through adaptive/predictive charging and for the power grid to achieve multiple operational objectives simultaneously
The use of EVs for providing ancillary services to the power system can be an additional revenue for EV owners and can assist the integration of larger amounts of renewable sources
Utility-scale batteries can be used for frequency controlled reserves due to their fast response time (pilot projects existing in Finland)
The Smart Grid Working Group has proposed market-based approach for demand flexibility with more dynamic load control to be implemented at latest on 30.3.2021

## Slide 9: Conclusions
Power balance = steady frequency  good power quality
Forecasting of demand and consumption
Frequency control mechanisms

## Slide 10
Questions?

## Slide 11: References
Aalto University, 2019. John Millar. Course material: ELEC-E8406 Electricity distribution and Markets
ENTSO-E, 2004. Load-frequency control and Performance. Appendix 1.
Fingrid. Reserves and control electricity. [Online source]. Accessed 15.3.2019. Available: https://www.fingrid.fi/en/electricity-market/reserves_and_balancing/
Fingrid. Balancing markets. [Online source]. Accessed 15.3.2019. Available: https://www.fingrid.fi/sahkomarkkinat/sahkomarkkinoiden-tulevaisuus/askelmerkit-sahkomarkkinamurrokseen/pohjoismainen-tasehallinta-ja-uudet-pohjoismaiset-markkinapaikat/
Thingvad, A. Economic value of electric vehicle reserve provision in the Nordic countries under driving requirements and charger losses. Journal of Energy Storage. 2019.