## Slide 1: ELEC-E8423 - Smart Grid Interconnection of microgrid to the Power system
Waleed Iftikhar
Michel Mabano
23.04.2018

## Slide 2: Introduction
Microgrid consist of DER, loads in a defined electrical boundary; can be controlled as a single unit with respect to the grid. according to IEEE Std 2030.7
Microgrid can be operated in a grid connected mode, islanded mode.
Loads in a microgrid are categorized into :
Priority
Critical
Controllable
Interruptable,
Dump and diversion

## Slide 3: Benefits and Motivation
Benefits offered by a microgrid
Access to power in remote location, lower cost and environmental impact
Deferral of investment in upgrading and renovating distribution grids
Grid resiliency, increased reliability, energy efficiency, Improved power quality, etc..
Motivation for connecting to the power system
Reduction of the energy storage need/capacity
Power system can act as an additional source to the microgrid, etc...

## Slide 4: Microgrid Structure

## Slide 5: Microgrid Control System
Microgrid control system should have real time control and energy management functions that operate in the following situations
Operation in grid-connected and islanded modes
Automatic transition from grid-connected to islanded mode
Resynchronization and reconnection from islanded mode to grid-connected mode
Energy management to optimize both real and reactive power generation and consumption
Ancillary services provision, support of the grid, and participation in the energy market and/or utility system operation, as applicable

## Slide 6: Interconnection of microgrid to the main grid
According to IEEE Std 1547
Connection of DERs must not cause voltage fluctuations higher than ±5% at the PCC.
Monitoring system for real output power, reactive power, and voltage at the point of connection for 250 kVA and above`
Grounding of the microgrid must not lead overvoltages of the equipments in the main grid.
Following fault in the EPS circuit connected to the microgrid
A microgrid shall detect unintentional islanding and cease to energize the EPS.
Reconnection may occur 5 minutes after voltage, frequency stabilized in the main grid.
Amendments in ( IEEE std 1547-2018)
DERs shall ride through abnormal V/f for a specified time .
DERs shall be able to regulate voltage by changing the reactive power.
DERs shall be capable of changing real power following frequency deviations.

## Slide 7: Hierarchial control levels of a microgrid
(” Basic Considerations for Integration of Microgrid Systems ”, 2018)

## Slide 8: Communication protocols and architecture
All the units in a microgrid coordinate with controller through communication channels.
Communication system in a microgrid is influenced by the control system architecture(whether it is centralized or decentralized).
Communication channels are characterized by data rates, spectrum, and coverage range, latency, etc ...

## Slide 9: Available communication to microgrid
(“Survey of Communication System for DG’s and Microgrid in Electrical Power Grid”, 2016 )

## Slide 10: Microgrid Pilot (St Julien en quint)
Motivation
Regular power outage due to storm
Stage I
45 clients defined in the boundary
Stage I concluded with annual power consumption measurements(10 min interval).
Among scenarios being studied
Maximum PV production
Optimal local production
ESS and DR .

## Slide 11: Conclusions
In grid-connected mode, a microgrid is seen as a single controllable unit, from the main grid perspective.
microgrid connection to the main grid side must not lead to negative impacts at the PCC.
Control system architecture will dictate the communication solutions.

## Slide 12: Source material used
https://ieeexplore-ieee-org.libproxy.aalto.fi/stamp/stamp.jsp?tp=&arnumber=8038773
https://ieeexplore.ieee.org/iel7/8295081/8295082/08295083.pdf
https://www.ieee.ch/assets/.../IEEE-Swiss-IES-Microgrids-ABB.pdf
ieeexplore.ieee.org/abstract/document/5960751/
https://ieeexplore-ieee-org.libproxy.aalto.fi/stamp/stamp.jsp?tp=&arnumber=7832732
https://www.academia.edu/34678706/Survey_of_Communication_System_for_DGs_and_Microgrid_in_Electrical_Power_Grid
www.ieomsociety.org/paris2018/papers/107.pdf
www.enrauvergnerhonealpes.org/fr/reseaux/.../le-projet-pegasus.htm