## Slide 1: ELEC-E8423 - Smart Grid Methods for Fault Location and Detection in Smart Grids April 10, 2018
Seppo Borenius, Muhammed Tuncag
10.4.2018

## Slide 2: Methods for Fault Location and Detection in Smart Grids - Introduction
Fault [1,2]:
  Shunt fault
    line-to-ground fault (short circuit between line and ground) or line-to-line fault (short circuit between two lines) or a combination of these
    Single-line-to-ground fault is the most common fault in distribution networks [3]
  Series fault, e.g. an open connector
“Fault location is a process aimed at locating the occurred fault with the highest possible accuracy. A fault locator is mainly the supplementary protection equipment, which apply fault-location algorithms for estimating distance to fault. A fault-location function (fault locator) can be implemented e.g. into protective-relays, digital fault recorders (DFRs), stand-alone fault locators, separate fault locators or post-fault analysis programs.” [4]
“Fault locators are used for pinpointing the fault position accurately and not only for indication of the general area (defined by a protective zone) where a fault occurred – which is the case with protective relays.” [4]

## Slide 3: Overall Structure of a Fault Location System [5]
DG = Distributed generation
SCADA = Supervisory Control and Data Acquisition
AMI = Advanced Metering Infrastructure
. . .
Load
Load
DG
DG
Load
Substation
Measurement
device
Distribution management system
Switching status Voltage and current measurements
Load data
Power network topology
Topology processor
State estimator
Fault location system
Collected information through SCADA, AMI, and other monitoring systems

## Slide 4: Fault Location and Fault Area Location Inputs and Outputs [6]

## Slide 5: Impedance Based Fault Location Methods [1]
Fault location is proportional to the impedance
Vf = voltage during fault, If = current during fault, Zl = line impedance per unit length, fd= Fault distance from measurement node

## Slide 6: Travelling Waves-Based Fault Location Methods
“When a fault occurs, it generates high frequency travelling waves of currents and voltages propagating away towards both ends” [6]. “Then, the travelling waves are reflected at the end of the line respectively [7]
Double-ended methods [8]
d= distance to the fault point from Bus1 (see picture) , v = propagation velocity of the travelling wave, l = line length, t11 = the initial transient instant at Bus 1,
t21 = the initial transient instant at Bus 2;
Single-ended methods [9] based on two consecutive reflections at the same end. This method does not require synchronization between the two ends.
x = the distance to the fault, v = the wave velocity (for the mode
used), and td = the time difference between two consecutive
peaks
Source: [5]

## Slide 7: Learning Based / Artificial Intelligence (AI) Based Fault Location Methods
Some AI methods which have been deployed in fault location in distribution systems [1]
  Artificial neural network (ANN)
  Support vector Machine (SVM)
  Fuzzy Logic
  Genetic Algorithm (GA)
  Matching approach
Case ANN
  Intend to replicate the way that we humans learn
  Recognizes difficult patterns of information but require a training process to locate a fault with a set of data input and expected output [1]. This input data can be acquired e..g through a digital fault recorder, a digital relay or even with computer simulations of the system model [10]

## Slide 8: Fault Location Utilizing Wide Area Monitoring Systems in Combination with Artificial Intelligence [11]
Phasor Measurement Units (PMUs) are power systems devices which are capable of measuring phasor values of voltage and current with time references provided by GPS
Major Components of a Wide Area Monitoring System (WAMS) are PMUs, Phasor Data Concentrators (PDC), Super-Phasor Data Concentrator (SPDC) and communications network.
In [11] WAMS and ANN technologies were combined: WAMS collects the data (phasors etc) and a trained ANN identifies if the system is in faulted condition and localizes the fault. The ANN system is very powerful in identifying the faulty pattern and classifying the fault by patter recognition.
GPS = Global Positioning System
ANN = Artificial Neural Networks

## Slide 9: Fault Location and Protection Challenges Introduced by Distributed Generation
Bi-directional power-flow [5,12]
  Numerous sources for fault current make protection and fault location more complex
  Case auto reclosure [11]: Auto reclosure unsuccessful since the distributed generator keeps feeding current and maintains the arc.
Limited fault currents due to power electronics which is often used to connect renewable generation to the power grid [12,13]
  Difficult to detect for protection applications. Line differential protection could be a potential solution. It requires a communication channel between he ends of the line. Currently this is implemented as optical fiber but going forward it could also be a 5G link. [12]

## Slide 10: Methods for Fault Location and Detection in Smart Grids - Conclusions
Integration of distributed, intermittent generation and microgrids, which can be operated either in grid connected mode or stand-alone modes, complicate fault location [6]
Evolving smart grids will be providing better measurement (PMUs, WAMS, AMI,…) and communications (4G,5G, …) infrastructure. Fault location algorithms can utilize this to provide better results [6]
Accelerating utilization of information technology, big data and artificial intelligence providing new opportunities for fast fault location and detection in complex networks, also for those containing distributed, intermittent generation
PMU = Phasor Measurement Unit
WAMS = Wide Area Monitoring System AMI = Advance Metering Infrastructure

## Slide 11: Source Material Used
[1] S.S. Gururajapathy, H. Mokhlis, H.A. Illias: Fault location and detection techniques in power distribution systems with distributed generation: A review, Renewable and Sustainable Energy Reviews 74, 2017, 949–95
[2] Jorma Elovaara, Liisa Haarla: Sähköverkit I, Otatieto 2011, 520 pages.
[3] E. Lakervi, E.J. Holmes: Electricity Distribution Network Design,Institute of Engineering and Technology, London 2007.
[4] Murari Mohan Saha, Jan Izykowksi: “Fault Location on Power Networks”, Springer-Verlag London Limited, 2010, 431 pages.
[5] Biswarup Das: Power Distribution Automation, The Institute of Engineering and technology, London, 2016, 339 pages.
[6] A. Bahmanyar, S. Jamali, A. Estebsari, E.Bompard: “A comparision framework for distribution system outage and fault location methods”, Electric Power System Research 145, 2017, 19-34
[7] Mohd Rafi Adzman: “Earth Fault Distance Computation Methods Based on Transients in Power Distribution Systems”, Doctotal Dissertation, Aalto University, 2014.
[8] F. V. Lopes, D. Fernandes Jr., W. L. A. Neves: Fault Location on Transmission Lines Based on
Travelling Waves, International Conference on Power Systems Transients (IPST2011) in Delft, the Netherlands June 14-17, 2011
[9] Fernando H. Magnago, Ali Abur: Fault location using wavelets, IEEE Transactions of Power Delivery, 1997
[10] Arturo Suman Bretas, Luciano Pires, Miguel Moreto, and Rodrigo Hartstein Salim: A BP Neural Network Based Technique for HIF Detection and Location on Distribution Systems with Distributed Generation, International Conference of Intelligent Computing 2006.
[11] D. Deveraj, M. Krishna Paramathma, I.Rajalakshmi: Simulation And Implementation of Phasor Measurement Unit for Wide Area Monitorin System, IEEE International Conference on Intelligent Techniques in Control, Optimization and Signal Processing, 2017.
[12] Kari Mäki, Pertti Järventausta, Sami Repo: Tuulivoimaan perustuvan hajautetun sähköntuotannon vaikutus sähköverkon suojaukseen, Tampereen Teknillinen Yliopisto, 2003.
[13] Gargi Bag, Linus Thrybom, Petri Hovila: Challenges and opportunities of 5G in power grids, 24th International Conference on Electricity Distribution, Glasgow 2017.

## Slide 12: Thank you!
Methods for Fault Location and Detection in Smart Grids