## Slide 1: ELEC-E8423 - Smart Grid Self-healing networks; automatic switching applications (FLIR)
Janne Lappi
Jaana Suontausta
07.02.2018

## Slide 2: Introduction
Self-healing concept
FLIR: Fault Location, Isolation and Restoration
Target to lower costs and improve reliability in distribution network
Fault management procedure
Short circuits: phase to phase
Earth faults: phase to ground
DA Distribution automation
Intelligent devices and remote controlled switches in secondary substations
DMS Distribution management system (collection of applications to monitor & manage the distribution network)
SCADA Supervisory Control and Data Acquisition (“traditional” computer-based supervisory & control system )

## Slide 3: Why self-healing
Self healing and DA are smart methods for improving reliability
  Option for traditional network investments
Target is to minimize costs: CIC (and DA implementation)
  Automatic fault management actions far faster than manual switching, 1s/1 min vs. 1 hour
  Optimal location and amount of automatic switches to be analyzed
70-80% of interruptions in Europe are caused by failures in MV network
  Focus on urban areas, where high electricity density
  On urban areas MV network is often meshed (but operated radially) -> backup connections exist
Notes: Focus should be on MV-voltage urban core areas, where high electricity density and high CIC’s.
Growing need for better service reliability besides aging infrastructure and limited budgets.
With DA the restoration of unfaulted segments can occur in less than one minute instead of 50-80 minutes

## Slide 4: Self healing – centralized or decentralized
Centralized system: DA combined with DMS and SCADA
  DA units gather and handle locally measured data
  DMS analyzes fault indication data, network topology and switch states and makes a plan on switching actions
  Operates fully automated or supported by a control center operator, depending on the automation level of the system
  SCADA system executes switching sequence in practice
Decentralized stand alone systems
  Smart DA units execute switching independently of the control centre
  Possibilities in micro grids?
In both cases, reliable and fast communication between DA units is required
System testing is difficult in a live network -> factory testing, network simulators
Safety issues: self-healing scheme must be disabled in case of an unstable network, unknown switch positions, telecommunication fault or a DA unit switched in local control mode (maintenance)
Notes: Fully automatic: Once the self-healing strategy is generated, the control signals for the breakers are distributed directly without human intervention
Semi-automatic: Once the self-healing strategy is generated, it must be confirmed by system operators first, and
then the control signals are distributed.

## Slide 5: Fault management – different fault types
Short circuit faults
Cause high fault currents
Secondary substations are already equipped with short circuit indicators
Faults are easy to locate
Earth faults
MV networks typically isolated or compensated, earth fault current very low
Sustained operation can cause earth fault to evolve into multiple faults, isolation is needed
Fault locating done by manual switching actions, which may involve several trials
Switch onto fault causes new interruptions on restored load points, repetitive power on-off situations are harmful to customer’s devices
Fault indication data can only be gathered from protection relays or from DA
Intelligent earth fault indicators are needed
Fault management procedure is not 100% satisfactory until the network is fully automated
Notes: Pääajatuksena se että oikosulkuja varten on olemassa jo hyvä fault location tapa mutta DA:ta toteutettaessa kiinnitettävä huomiota maasulkuihin.

## Slide 6: Fault management - switching actions [2]
If no fault detection in a S/S, the fault is located upstream. Upstream switch shall be opened if the fault is not already isolated by adjacent substation
If detectors indicate fault within a S/S (e.g. faulty cable termination), system shall open the switches in the two neighbouring substations too
If the fault detectors indicate downstream fault, the downstream switch shall be opened if the fault is not already isolated by adjacent substation
If the fault upstream of the normal open point has been isolated, it is safe to close the open point
If the fault downstream of the primary substation has been isolated, it is safe to reclose the circuit breaker
Notes: Reference Architecture for Self Healing Distribution Networks, Tom Berry and Yves Chollot Schneider-Electric.
Principles of self-healing algorithm.

## Slide 7: Example of self-healing system – Circuit Breaker [3]
Protection example for CB
3-phase overcurrent (instantaneous, time delayed)
Undirectional earth fault current
Directional earth fault current (Uo measurement)
Thermal overload (cable)
Under/overvoltage
Auto reclosing and SYNC check/voltage check
Notes: Circuit breaker can break (or switch) fault current, expensive, typically used in primary substation. Directional protection functions need voltage measurement.
Other protection elements: Fuse failure supervision, Frequency based load shedding, Line differential relay.

## Slide 8: Example of self-healing system- Switch [3]
Fault Indication elements for recloser or switch
Similar than for CB, e.g.
3-phase overcurrent
Directional earth fault current (Uo measurement)
  BUT
VT’s are expensive -> Current based methods needed [1]
Zero sequence threshold
Negative sequence comparison
Notes: In practise the reclosers are often replaced by cheaper manually or remote controllable switches, which can not break or make fault current.
Osmo Siirto:”Along the fault current path between the feeding substation and the fault point, the negative sequence component varies only a little, but it is practically non-existent behind the fault.”

## Slide 9: Conclusions
Target
Fast automatic actions in case of a fault -> Lower CIC, higher reliability
Option for traditional investments
Urban areas most beneficial
High CIC
Meshed MV network
Optimisation of DA unit layout in the network
Centralized or decentralized automation
Centralized system is easier to implement
Decentralized might be good in the future
Reliable telecommunication needed
Comprehensive factory testing with network simulators
Calibration of earth fault indication (without VT’s) is challenging
Notes: Osmo Siirto: “Ignoring the impact of earth faults and fault management procedure can lead to suboptimal DA implementation.”

## Slide 10: Source material used
[1] Doctoral Dissertation: Osmo Siirto, Aalto University
Distribution Automation and Self-Healing Urban Medium Voltage Networks
[2] Tom Berry and Yves Chollot Schneider-Electric
Reference Architecture for Self Healing Distribution Networks
978-1-5090-2157-4/16/$31.00 ©2016 IEEE
[3] Doug Voda, David Frame, Wei Huang, Alfredo Romero and Harsh Karandikar ABB Inc.
Reducing System Losses and Implementing Self- Healing to Minimize Impact of Faults in Distribution Networks
[4] Yufeng Lin, Mingjie Sun, Yiyun Guo, Yongzhi Chen, Junyan Gao, Xiaowen Yu, Juanjuan Li, Bo Hong, Hongkun Chen, Yanwen Wu, Feixiang Huang, Jibin Lin, Fengyuan Zheng, Da Li, Xiaohui Wang, Dele Huang, Meijiao Zheng, State Grid Xiamen Electric Power Supply Company, China
Towards a Real-Time Fault Identification and Self-healing System in the Distribution Network
978-1-5386-3917-7/17/$31.00 ©2017 IEEE