## Slide 1: ELEC-E8423 - Smart Grid Demand response in power system energy balance management
Jari Heimonen
15.02.2018
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 2: Introduction
Demand Response has come to focus in power systems due to the increased share of variable renewable energy sources like wind and photovoltaic power.
Aim of this presentation is to give an overview of the power system energy balancing management and how the demand response reserves and markets are used for the balancing.
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 3: Frequency and balance
The balance between production and consumption is indicated by the frequency of the electricity grid.
The frequency falls when consumption is greater than production and increases when production is greater than consumption.
Frequency variation requirements:
  In Nordic countries the frequency is allowed to fluctuate between 49.9 and 50.1 Hz in normal state (nominal value 50 Hz).
  Allowed 10 s average variation
    49,5 Hz – 50.5 Hz ; 99,5 % during the year
    47 Hz – 52 Hz ; 100 % during the year
  Defined in standard: SFS-EN 50160
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 4: Forecasting the consumption and production
In Finland TSO (Fingrid) creates the energy consumption forecast plan for the each hour of the next day.
The market operators plan their production in advance for the next day correspondingly and provide the plan to the TSO.
  Planning is based on the information from consumption forecast and realized bids in the day-ahead Elspot-market.
Example of the load and generation
forecasts (MWh) In Finland during
5.2. - 11.2.2018:
Consumption forecast
Generation forecast
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 5: Reserves
Even the consumption and production has been planned in advance, in practice there are some deviations during each hour.
To balancing these deviations, TSO procures different kinds of reserves from reserve markets.
  Reserves are power plants and consumption resources which either increase or decrease their electric power according to the need of the power system.
Demand response reserves and balancing markets are mainly used for the maintaining of the hourly power balance.
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 6: Reserve types maintained by Finnish TSO
Reserve | Name | Minimum Size MW* | Activation times
Frequency Containment Reserve for Normal Operation | FCR-N | 0,1 | Continuously in frequency span 50,1-49,9 Hz. 0,1 Hz change 100% in 3 min. (Activation: local frequency measuring)
Frequency Containment Reserve for Disturbances | FCR-D | 1 | Linearly in frequency span 49,9-49,5 Hz. Below 49,5: Hz 50% in 5 s and 100% in 30 s. (Activation: local frequency measuring)
Automatic Frequency Restoration Reserve | aFRR | 5 | After receiving a request, 100% in 2 min. (Activation signal from TSO)
Manual Frequency Restoration Reserve | mFRR | 10 / 5** | According to the bids in balancing power market. 100% activated in 15 min. (Activation signal from TSO)
* Minimum reserve size to participate to the reserve markets
** 5 MW if using electronic activation
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 7: Balancing
Market operators plan and balance their consumption and production in advance for the next day correspondingly.
In Finland the TSO is responsible to take care of the balance between consumption and production during each hour.
TSO ensures the balance by activating regulating bids from the balancing power markets and by reserving capacity.
TSO has also the own power plants and leased power plants which are not used for commercial electricity production.
  These peak load reserves takes care of the reliable supply of electricity in situations where a planned purchase of electricity is insufficient to cover the forecast consumption of electricity.
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 8: Conclusions
The balance between production and consumption is indicated by the frequency of the electricity grid.
Market operators plan and balance their consumption and production in advance for the next day correspondingly. TSO is responsible to take care of the balance between consumption and production during each hour.
Demand response reserves and balancing markets are used for the maintaining of the hourly power balance.
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management

## Slide 9: Source material used
Jarmo Elovaara and Liisa Haarla, 2011, Sähköverkot I, Otatieto, Espoo, Finland.
Fingrid, https://www.fingrid.fi/en/electricity-market/
Fingrid, PDF-document, Reservituotteet ja reservien markkinapaikat, https://www.fingrid.fi/globalassets/dokumentit/fi/sahkomarkkinat/reservit/reservituotteet.pdf
Matti Lehtonen, 2018, Advanced Power Engineering Book Chapter 42, Espoo, Finland
Energy authority, https://www.energiavirasto.fi
ELEC-E8423 – Smart Grid
Demand response in power system energy balance management