## Slide 1: ELEC-E8423 - Smart Grid Photovoltaic hosting capacity of low voltage and medium voltage grids, 27.3.2018
Eero J.Paavilainen
Antoni Kopaly

## Slide 2: Introduction
Green energy and renewables are rising as energy production forms
  Photovoltaic (PV) systems are going to be one of the main sources of green energy
  70 % of this PV capacity is Europe is integrated into low voltage (LV) networks
This PV integration creates problems in the LV-network
  Voltage rises, unequal distribution of PV on different phases, unbalances
  Loading constraints of the networks (transformers/cable ampacity)
In order to avoid the problems, efficient methods of voltage control are needed

## Slide 3: Closer look at the problem
Voltages usually well balanced at the supply side level (HV- and MV-level)
Voltages at the customer level (LV) can become unbalanced due to the unequal system impedances and distribution loads
  Can result in overheating in grid components and transformers
Standard SFS-EN 50160 states that 95% of the time, voltage at LV-level should be 230V±10% and voltage unbalance should not exceed 2% at 95% of the time
Growing interest by the residential customers to install single-phase grid-connected rooftop PV cells (creating distributed generation DG networks)
  PV’s output power being fed to the grid is not controlled and is dependent on the instantaneous power from the sun
  Many times the PV’s are single phased
      Both causes problems
Distribution Network Operators (DNO’s) also have to critically review the loading constraints of the network (transformer loading and cable ampacity) before deciding on PV inclusion.

## Slide 4: How to solve these problems = Increase hoisting capacity
Different study cases have been done with simulations to improve the PV hoisting capacity
These studies have been using Monte Carlo based approach to study distribution networks in rural and urban areas with different variables:
  Both single and three-phase PV generation
  Using voltage regulation at transformer by on load tap-changer (OLTC)

## Slide 5: Study case 1: Network PV Hosting Capacities (Without OLTC)
In balanced 3-phase feed-in , the limiting constraint are mostly:
  over voltage, transformer loading violation
In unbalanced 1-phase feed-in, the limiting constraint are mostly:
  high voltage unbalance, neutral wire violation or transformer loading violation
Result: The calculated PV hosting capacity in single phase connections are signiﬁcantly lower than in the balanced feed
PR = Predominant Rural
IN = Intermediate
PU = Predominantly Urban

## Slide 6: Study case 2: Network PV Hosting Capacities (With OLTC)
In study case 1, over-voltage was the primary limiting constraint in 6 out of 18 cases. This can be mitigated by active voltage control
For balanced network, using OLTC, the over-voltage constraint changed into to transformer loading constraint in every case
For unbalanced network, the hoisting capacity increased a little, but the unbalance problem stayed as the main constraint.
Results: Using OLTC can significantly increase hosting capacity in balanced feed.
In the single-phase feed, the voltage unbalance and neutral wire ampacity violation remains the main issues.
PR = Predominant Rural
IN = Intermediate
PU = Predominantly Urban

## Slide 7: Further discussion
DC distribution replacing AC
Energy metering infrastructure ( how much and where)
How often to use active voltage control (OLTC)
  wearing of transformers etc
Lack of standards and long term experience in the topic area

## Slide 8: Conclusions
Hosting capacity of Finnish low voltage networks is considerably high as long as PV generators are connected in a balanced way.
Unbalanced however reduces the hosting capacity enormously.
With active voltage control, big possibilities to increase hosting capacity in balanced feed

## Slide 9: Source material used
An Analysis of Photo-Voltaic Hosting Capacity in Finnish Low Voltage Distribution Networks. Arshad, Lindner and Lehtonen (2017)
Sensitivity analysis of voltage imbalance in distribution networks with rooftop PVs. Farhad, Ritwik, Arindam, Ledwich, Gerard and Firuz (2010)
Industrial aspects of voltage management and hosting capacity of photovoltaic power generation in low voltage networks. Rauma (2016)
Limits of PV hosting capacity in low voltage networks. Linder (2016)