## Slide 1: ELEC-E8423 - Smart Grid Solar farms, their local grids and connection to the power system
Billah Md Masum
24.04.2018

## Slide 2: Introduction
Solar Farm- Collection of solar panels on land in order to generate electricity to feed into the grid. Due to the lack of a standardized definition for solar farms, most industry representatives and government agencies refer to solar farms as utility-scale solar. Solar farms at the utility scale will typically be at least 1 megawatt (MW), which is a power plant capable of supplying some 200 households.
Area of Solar Farm: 4 acres if it uses crystalline solar panels without trackers ( 1MW solar farm)
6 acres if it uses thin film solar panels without trackers ( 1MW solar farm)
Installation Cost : Around $ 0.80- $1 per Watt ( utility-scale solar)
1 MW solar farm would roughly cost Approx. 1 million USD
Around $3-$4 per Watt ( Residential Solar)
“Solar farms, their local grids and connection to the power system”

## Slide 3: Global Cumulative Installed Capacity and Solar PV market shares
After the 300 GW milestone was reached in 2016, we expect that the install capacity will be exceed 400 GW in 2018, 500 GW in 2019, 600 GW in 2020 and 700 GW in 2021.
China was dominating solar market in 2016 which officially added 34.2 GW, over 125% more than in 2015. USA was added 14 GW up from 7.3 GW the year before. European countries installed 6.9 GW which 20 % less than the previous year.
Chart: Global solar PV market shares in 2016
| China | USA | Japan | Rest of World | Europe | India
 | 0.45 | 0.19 | 0.11 | 0.1 | 0.09 | 0.06
“Solar farms, their local grids and connection to the power system”
Global Cumulative Solar PV Installation Capacity

## Slide 4: Solar Power in Europe
Solar Electricity Generation in Europe from 2010 to 2017 (including split of top 5 countries)
-Only 8.8 GW of solar was installed in 2017 that is 2 GW more than in 2016 but 13.9 GW less than peak installed in 2011.
- Once a solar leader, EU’s solar market is in danger by the Asian powerhouses such as china in both solar installation and production.
-Generation from solar increased by Only 8 TWh in 2017.
The reason is the low rate of new capacity installation.
Germany is leading on solar energy generation in Europe.
“Solar farms, their local grids and connection to the power system”
Annual Solar PV installation in Europe

## Slide 5: Grid Connected PV System
small system <10 kW & intermediate system 10kW-500kW are installed at distribution side.
large system greater than 500 kW is installed at transmission side.
Inverter: Inverter not only has DC to AC switching function, it also has other functions-
-Initiative operation and stop.
-maximum power point tracking (MPPT) control.
-anti-independent operation function.
-active voltage regulation function.
-DC detection function.
Inverter starts operation initiatively, when the output power of solar module reach the inverter required power.
Inverter choose a best point of maximum voltage and current to produce maximum power from the solar cell module.
“Solar farms, their local grids and connection to the power system”
Grid Connected PV System

## Slide 6: Grid Connected PV System (Cont.…)
Plant Controller: A control tool that serves to regulate certain parameters on plant, either directly or through the PV SCADA solution. It operates independently of the monitoring and control of the energy plants.
Supervisory control and data acquisition (SCADA) System: SCADA is used to monitor the Solar energy plant. This system is able to take in different sensor readings, whether forecasting's, generate remote site alarms for faults as well as transfer data to a centralized location for storage or report generation.
A real time controller will connect to remote I/O to collect the data from Inverter and current PV from the combiner box and also included is the alarm of surge detection in the box.
The controller will send all data to server via GPRS modem and store all of the data into memory. In case the network GPRS is down, the controller will store the backup data and will send the backup data to the server whenever the network is recovered.
“Solar farms, their local grids and connection to the power system”

## Slide 7: Impacts of Grid Connected PV System on Distribution Networks
Reverse power flow: Net Production > Net Demand, especially at noon. Power flows to LV side to MV side and cause overloading of the distribution feeder and excessive power losses.
Overvoltage along distribution feeder: Reverse power flow leads to overvoltage along distribution feeder. Voltage regulators and capacitors bank is used to boost voltage slightly now push voltage further ( above the acceptable limits).
Voltage control difficulty: voltage control is a difficult task due to the existence of more than one supply point. Voltage regulating devices are designed to operate in a system with unidirectional power flow.
Phase Unbalance: most inverters in residential PV system are single phase. If this inverter are not used evenly among different phases, phase unbalance may be takes place shifting the neutral voltage to unsafe value and increasing the voltage unbalance.
Increased reactive power: In PV system, inverters are openly operating at unity power factor to maximize active power generation. As a result, the active power required for existing loads are partially met by PV system, reducing active power supply by the utility. But the reactive power is still same, thus, distribution transformer operate at low power factor and it reduces overall system efficiency.
“Solar farms, their local grids and connection to the power system”

## Slide 8: Control System of Solar Power Plant
An optimal PV plant appears to the grid as a single unified source of power by balancing two modes of operation- Active Power Control (APC) and Automatic Voltage Regulation (AVR).
APC limits generation at the POI ( Point of Interconnection) to predetermined setpoint. Grid support through AVR is done by regulating reactive power.
The plant set point at the POI is determined by the operator, grid demand and output potential.
The PID controller constantly compares the current setpoint with the actual value as it appears on the grid.
Discrepancies between the current setpoint and instantaneous output manifest as an error which is used to correct the output.
If there are more solar irradiance than needed to maintain a setpoint, the inverters are commanded to limit themselves. Purposeful limitation of production is called “Curtailment”.
Inverters which are affected by cloud cover only produce the power available from their limited irradiance, but other inverters can produce more than their fare share to compensate.
“Solar farms, their local grids and connection to the power system”

## Slide 9: Conclusion
Global solar installation capacity is increasing rapidly (nearly 1 TW solar installed capacity is possible by 2021). But the installation capacity is decreasing significantly in Europe day by day.
The control system acts in accordance with two major directives; ”Active Power Control (APC)” monitors and curtails the active power harvested from the PV arrays and Automatic Voltage Regulation (AVR) monitors and controls of reactive power produced and absorbed for the Grid.
PV solar facilities are the most reliable when they are invested in predictable, redundant and secure practices.
“Solar farms, their local grids and connection to the power system”

## Slide 10: Source material used
Solar Power Europe, “Global Market Outlook for Solar Power 2017-2021”, Africa-EU Renewable Energy Cooperation Program(RECP),Available on: www.solarpowereurope.org
Dave jones, Dr.Alice sakhel,Matthias Buck and Dr.Patrick Graichen.2018. “ The European Power Sector in 2017”, Available on: www.sandbag.org.uk
Solar Inverter, Available on: www.solar.inverter.co
Danielle Silva, “SCADA Patterns & Best Practices for Utility Scale Solar PV – Power Plant Control”.
Ranon Satitpanyapan,” SCADA and Monitoring for Solar Energy Plant”, Bangkok,Thailand.
Davud Mostofa Tobnaghi.2016.” A Review on Impacts of Grid-Connected PV system on Distribution Network”
https://news.energysage.com/solar-farms-start-one/
http://www.suncyclopedia.com/en/area-required-for-solar-pv-power-plants/
“Solar farms, their local grids and connection to the power system”