## Slide 1: ELEC-E8423 - Smart Grid Wind farms, their local grids and connection to the power system
Adithya V

## Slide 2: Wind energy integration Statistics–EU
Reference: https://windeurope.org/about-wind/statistics/

## Slide 3: Wind Farm On-shore & Off-shore Statistics–EU
Reference: https://windeurope.org/about-wind/statistics/

## Slide 4: Wind power Integration to the Power system
Wind power generation does not produce harmful emissions. But with random nature
of wind resources, the wind farm generates fluctuating electric power.
These fluctuations have a negative impact on stability and power quality in electric
power systems. Large scale Integration of DG units in the distribution grid not only
affects the grid planning but also has an impact on the operation of the distribution
grid.
Aspects which are influenced by the connection of DG units are:
Power Quality
Voltage Control
Grid Losses
Fault Level
Protection System.

## Slide 5: Major impacts of integrating wind energy into the grid
Figure: Major potential technical impacts of integrating wind energy into the grid
Technical impacts on Power Quality
Poor Power Factor
Voltage sags
Flickering
Harmonics
Voltage surges
Voltage dips
Reactive Power Compensation
Voltage fluctuations / Instability
Notes: VOLTAGE VARIATION
A system experiences a state of voltage instability when
there is a progressive or uncontrollable drop in voltage
magnitude after a disturbance, increase in load demand or
change in operating condition. If a large proportion of the
grid load is supplied by wind turbines, due to output
variations wind speed changes which can cause voltage
variation and this affects the normal operation of system[9].
The voltage variation can occur in specific situation mainly
as a result of load change and these canbe expected
particularly in the case of generator connected to the grid at
fixed speed. The large turbine can achieve significantly
better output using variable speed operation, particularly in
the short time range.
The Voltage dip is a very common and serious type of power quality disturbance due to its effects on sensitive equipment and industrial processes[10] . Voltage dip could occur when there is a large load such as motor start up, transformer energising, capacitor energising, switching of electronic load, momentary overload or a fault in the system network. It can cause the disconnection of wind generators, which could have a negative impact on the stability of the network due to loss of generation[11].It is a sudden reduction in the voltage to a value between 1% to 90 % of the nominal value after a short period of time, conventionally 1ms to 1 min.
This problem is considered in the power quality and wind turbine generating system operation and computed according to the rule given in IEC 61400-3-7 standard, ―Assessment of emission limit for fluctuating load‖. The relative % voltage change due to switching operation of wind turbine is calculated as
HARMONICS
Harmonics can be injected both at the generation and the consumer end. At the consumer end, harmonics are caused by non linear loads such as television, personal computers, compact fluorescent lamps, and so forth.The harmonics distortion caused by non-linear load such as electric arc furnaces, variable speed drives, large concentrations of arc discharge lamps, saturation of magnetization of transformer and a distorted line current. The current generated by such load interact with power system impedance and gives rise to harmonics. The effect of harmonics in the power system can lead to degradation of power quality at the consumer’s terminal, increase of power losses, and malfunction in communication system[12]. The degree of variation is assessed at the point of common connection, where consumer and supplier area of responsibility meet. The harmonics voltage and current should be limited to acceptable level at the point of wind turbine connection in the system. According to standard IEC61400-21 guideline, harmonic measurements are not required for fixed speed wind turbines where the induction generator is directly connected to grid. Harmonic measurements are required only for variable speed turbines equipped with electronic power converters. In general the power converters of wind turbines are pulse-width modulated inverters, which have carrier frequencies in the range of 2-3 kHz and produce mainly inter harmonic currents. The harmonic measurement at the wind turbine is problem due to the influence of the already existing harmonic voltage in the grid. The wave shape of the grid voltage is not sinusoidal. There are always harmonics voltages in the grid such as integer harmonic of 5th and 7th order which affect the measurements.
FLICKERS
The wind generators sometimes produce oscillatory output power, which could cause flickers in the power system network. Flicker is the one of the important power quality aspects in wind turbine generating system. Flicker has widely been considered as a serious drawback and may limit for the maximum amount of wind power generation that can be connected to the grid. Flicker is induced by voltage fluctuations, which are caused by load flow changes in the grid. The flicker is mainly produced by fluctuations in the output power due to wind speed variations. There are many factors that affect flicker emission of grid connected wind turbines during continuous operation, such as wind characteristics and grid conditions[12]. Variable-speed wind turbines have shown better performance related to flicker emission in comparison with fixed-speed wind turbines. The flicker study becomes necessary and important as the wind power penetration level increases quickly. Owing to smoothing effect, large wind turbine produced lower flicker than small wind turbines, in relation to their size.
The flicker level depends on the amplitude, shape and repetition frequency of the fluctuated voltage waveform. Evaluating the flicker level is based on the flicker meter described in IEC 61000-4-15. Two indices are typically used as a scale for flicker emission, short-term flicker index, Pst and long-term flicker index, Plt. Plt is estimated by certain process of the Pst values. It is assumed that wind turbines under study is running at normal operation; hence, the long-term flicker index (Plt), which is based on a 120-min time interval, is equal to Pst and, therefore, Pst is only considered in this work. The normalized response of the flicker meter described in Figure 2.

## Slide 6: Grid related challenges on different timescales
On short time scales (milliseconds to minutes),
the challenges relate to power quality issues,
such as stability of voltage and frequency.
On medium time scales (minutes to hours), the
scheduled production must meet the planned
demand and the electricity produced needs to
reach the load.
On longer time scales (weeks to
seasons), the production and transmission
capacity should be able meet demand in all
parts of the system over the whole year,
otherwise loads must be curtailed in order to
keep the system in balance.
Reference: https://www.google.fi/search?q=wind+farm+power+stability
Notes: As discussed in Chapter 5, there are several advantages of connecting the generation close to the end user, e.g. reduced losses. However, since electricity produced from solar and wind varies over the day, other challenges arise, both technical and economic. Additional challenges arise from the fact that the localisation of generation units are limited to certain areas, i.e. wind turbines are usually placed in windy areas and not where it is most suitable for the electricity grid, resulting in need for new transmission lines.1
There are no major technical limitations on the amount of wind and solar power that could be connected to the grid. However, there might be challenges that need to be considered depending on the characteristics of the energy source and the local conditions at the site where it is connected. At most sites, integration of small shares of wind and solar power require little adaptation of the electricity grid. As the shares increase, the need for adaptation increases and the integration costs may rise.
Rather than trying to provide an exact number of the maximum amount of renewable electricity generation that could be integrated, this chapter aims at highlighting the possible technical and economic challenges that may arise from integration of wind and solar power and how these challenges could be met.

## Slide 7: Impact of integration of Wind turbines at the Distribution Grid
In distribution systems when it comes to integration of wind energy the most prominent
challenges relates to voltage rise and overloading of System components. While also
other issues may arise from fluctuation in electricity production due to gusty winds.
Voltage rise issues emerge when the electricity generated exceeds the local demand,
causing the electricity to flow in opposite direction compared to normal operation. This
reversed power flow may also affect the protection system and cause overload in
system components.
There are different approaches to address these problems, e.g. reinforcement in the
distribution grid, demand side management (DSM), energy storage, energy curtailment,
reactive power compensation and coordinated on-load tap changer (OLTC) control.
Negative values here indicate that the power flow is in opposite direction to what is
indicated by the arrow (usually expressed as reverse power flow)
Figure: A simplified representation of a rural distribution system & The total load (PL), wind power in the system (PW), and the total (net) power flow (PT) measured at the substation
Notes: Both wind power and solar PV will affect the distribution system in similar ways; however there are some major differences. Firstly, the time variation of production differs and secondly the location where they are installed may vary. It is likely that a large share of the solar PV units will be connected to the low voltage distribution system due to its modular properties, allowing for integration in buildings and economic performance independent of scale. In Germany, about 70 % of the solar PV is connected to the low voltage distribution system.3 Although there are small scale wind turbines that, like solar PV, could be installed within the low voltage distribution system, wind turbines are more likely to be connected to the regional transmission system or to the medium voltage distribution system.
The amount of wind and solar PV that can be installed in a distribution system without violating the reliability and performance of the system depends on the design of the distribution system and on the load profile. Systems with a high mismatch between the electricity generation and demand will have more difficulties to cope with large penetration levels while systems with better load matching can facilitate larger shares. Similarly, systems designed for high peak demand can facilitate more PV and wind power than systems designed for a low peak demand since the system is designed to cope with higher power levels. Other concerns relate to the length of the distribution grid where long distances between the customer and the substation will likely experience increased voltage fluctuations and voltage rises during the day compared to a grid with shorter distances.
Electricity generated from solar PV is rather predictable and, on an aggregated level, it correlates with the demand on a daily basis. For countries with warm
To visualise the mismatch, Figure 9.2 presents the net power flow, i.e. the demand minus the generation, in a residential distribution system during a winter and a summer week for different levels of solar PV penetration. As can be seen, all electricity produced by the solar PV is consumed within the distribution system during winter times whereas the reversed power flow is substantial during summer time.
The electricity produced by wind turbines is usually less predictable on a daily basis. This stochastic behaviour can be seen in Figure 9.3, which presents the power output over a year from 13 wind turbines installed in a distribution system in the western part of Sweden, together with the load demand and net power flow. For countries with high electricity demand in winter, e.g. Sweden, there is a seasonal correlation between electricity generation from wind turbines and demand
Traditionally, the connection of solar PV and wind power at a given location in a distribution system is allowed after making sure that the installation does not cause overvoltage or overloading problem when it is producing at maximum power output and when the load in the system is at its minimum. However, due to the rare occurrence of minimum load and maximum power production, shown in Figure 9.3, this approach does not result in the efficient use of the system resources.
As can be seen in Figure 9.3, the power output from the wind farm is rarely above 10 MW and is never above 12 MW. Moreover the minimum system load observed is 0.5 MW, though the maximum wind power output can be as high as 12 MW, the maximum reverse power flow, noticed is 9 MW. This shows that, although the stochastic nature of electricity produced by wind turbines, the coincidence of maximum wind power output and minimum demand is rare. That is, the transformer is less likely to be overloaded due to reverse power flow. Hence, the distribution system can in reality withstand substantially higher penetration levels compared to only considering the maximum power output and minimum loading condition.
To allow further increase in penetration level of solar PV and wind power without reinforcing the distribution system active management strategies, such as, demand side management (DSM), energy curtailment, reactive power compensation, or coordinated on-load tap changer (OLTC), could be used. The principle of DSM is to schedule part of the demand such that overloading and voltage rise is avoided (Chapter 10) whereas energy curtailment avoids the problem by curtailing part of the wind or solar energy. Reactive power compensation and coordinated OLTC control is used in order to bring down the voltage in the distribution system, either by increasing the reactive power consumption by the wind turbines and PV inverters or by a voltage regulation mechanism at the substation transformer. However, this should be done with care, as it may lead to under-voltage in other feeders where wind turbines or PV are not installed.
A case study shows that by applying active management strategies, involving wind energy curtailment and coordinated OLTC control, the hosting capacity of the distribution system can be increased by as much as 83%, compared to the hosting capacity of the network without any active management strategies, with mere 3.3% energy curtailment. The reason for the low energy curtailment needed is due to the rare occurrence of high wind power production and low demand. This level of wind energy curtailment is also seen to be attractive compared to the traditional solution of grid reinforcement within the framework of the study. Similar to the PV study, this study does not consider impact on the upstream grid or short term voltage stability.7

## Slide 8: Conclusions
In response to the energy needs and environmental concerns, electricity from wind generators is considered as one of the future solutions.
However, the variability and the diffuse nature of the wind power can be challenging to the operation of a power system.
The wind turbines connected to weak grids have an important influence on power system.
The weak grid is characterized by large voltage and frequency variations, which affects wind turbines regarding their power performance, safety and allied electrical components.

## Slide 9: Source Material Used
Sharad W., Mohod,Mohan, V. Aware, ―Power Quality Issues and Its Improvement in Wind Energy Generation Interface to Grid System‖, MIT
International Journal of Electrical and Instrumentation Engg., vol.1,no.2,pp.116-122,2017
Doina Dragomir,‖The Aspects Related To The Grid Connection Of The Wind Farms Into National Power System‖,U.P.B. Sci. Bull.
Vol.73,no.1,pp.273-279,2011.
Z. Chen, ―Issues of Connecting Wind Farms into Power Systems‖, IEEE/PES Transmission and Distribution Conference & Exhibition: Asia and
Pacific Dalian, China,vol.II, 2005.