## Sheet1
Camino Medical Group - Mountain View Medical Office Building
MEP/FP Systems Installation
| Areas |  | Southeast |  |  |  | Southwest |  |  |  | Northeast |  |  |  | Northwest |  |  |  | Center
| Floor | Consumption Rate (man hours per unit) | 1 | 2 | 3 | Roof | 1 | 2 | 3 | Roof | 1 | 2 | 3 | Roof | 1 | 2 | 3 | Roof | 1 | 2 | 3 | Roof | Units | Optimal Crew Size | Subcontractor
Item
1 | Branch conduit | 0.064 | 3000 | 3000 | 3000 | 3000 | 2500 | 2500 | 2500 | 2500 | 3000 | 3000 | 3000 | 3000 | 2500 | 2500 | 2500 | 2500 | 1000 | 1000 | 1000 | 1000 | (lf) | 1 | Electrical
2 | Cable Tray | 0.053 | 250 | 250 | 250 | 250 | 160 | 160 | 160 | 160 | 250 | 250 | 250 | 250 | 160 | 160 | 160 | 160 | 50 | 50 | 50 | 50 | (lf) | 1 | Electrical
3 | Casework, Millwork | 0.2 | 2000 | 2000 | 2000 |  | 1300 | 1300 | 1300 |  | 2000 | 2000 | 2000 |  | 1300 | 1300 | 1300 |  | 1075 | 1075 | 1075 |  | lf | 2 | Casework
4 | Ceiling tile | 0.007 | 30000 | 30000 | 30000 |  | 20000 | 20000 | 20000 |  | 30000 | 30000 | 30000 |  | 20000 | 20000 | 20000 | [5 empty] | sq.ft. | 1 | Ceiling Tile
5 | Dom Water | 0.07 | 2000 | 2000 | 2000 |  | 1400 | 1400 | 1400 |  | 2000 | 2000 | 2000 |  | 1400 | 1400 | 1400 | [5 empty] | (lf) | 1 | Plumbing
6 | Doors & Hardware | 0.9 | 75 | 100 | 100 | 5 | 75 | 100 | 100 | 5 | 75 | 100 | 100 | 5 | 50 | 75 | 75 | 5 | 5 | 5 | 5 | 0 | No. | 2 | Doors, Frames Hardware
7 | Drywall | 0.013 | 36000 | 36000 | 36000 | 0 | 24000 | 24000 | 24000 |  | 36000 | 36000 | 36000 | 0 | 24000 | 24000 | 24000 | 0 | 8000 | 8000 | 8000 | 8000 | sq.ft. | 2 | Drywall
8 | Feeder conduit | 0.1 | 2000 | 2000 | 2000 | 2000 | 1500 | 1500 | 1500 | 1500 | 2000 | 2000 | 2000 | 2000 | 1500 | 1500 | 1500 | 1500 | 750 | 750 | 750 | 750 | (lf) | 1 | Electrical
9 | Fireproofing | 0.02 | 35000 | 35000 | 35000 |  | 24000 | 24000 | 24000 |  | 35000 | 35000 | 35000 |  | 24000 | 24000 | 24000 |  | 8000 |  |  |  | sq.ft. | 2 | Fireproofing
10 | Floor coverings | 0.018 | 30000 | 30000 | 30000 |  | 20000 | 20000 | 20000 |  | 30000 | 30000 | 30000 |  | 20000 | 20000 | 20000 |  | 5000 | 5000 | 5000 | 0 | sq.ft. | 2 | Flooring
11 | Frame priority fullheight walls etc. | 0.25 | 1000 | 1000 | 1000 | 0 | 650 | 650 | 650 | 0 | 1000 | 1000 | 1000 | 0 | 650 | 650 | 650 | [5 empty] | (lf) | 2 | Drywall
12 | Light Fixtures, Diffusers, Ceiling Mounted Trim | 0.5 | 464 | 464 | 464 | 450 | 354 | 354 | 354 | 350 | 464 | 464 | 464 | 450 | 354 | 354 | 354 | 350 | 100 | 100 | 100 | 100 | No. | 1 | Electrical
13 | Mechanical Rough | 0.1 | 1500 | 1500 | 1500 |  | 1000 | 1000 | 1000 |  | 1500 | 1500 | 1500 |  | 1000 | 1000 | 1000 | [5 empty] | (lf) | 1 | Mechanical
14 | MED GAS | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (lf) | 1 | Plumbing
15 | Medium pressure duct | 0.1 | 500 | 500 | 500 |  | 350 | 350 | 350 |  | 500 | 500 | 500 |  | 350 | 350 | 350 | [5 empty] | (lf) | 1 | Mechanical
16 | MEP Trim | 0.5 | 75 | 75 | 75 | 0 | 50 | 50 | 50 | 0 | 75 | 75 | 75 | 0 | 50 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | No. | 1 | Mechanical
17 | Paint | 0.008 | 36000 | 36000 | 36000 | 0 | 24000 | 24000 | 24000 |  | 36000 | 36000 | 36000 | 0 | 24000 | 24000 | 24000 | 0 | 8000 | 8000 | 8000 | 8000 | sq.ft. | 1 | Painting
18 | Rain Water Leaders, Waste and Vent | 0.04 | 2500 | 2500 | 2500 |  | 1700 | 1700 | 1700 |  | 2500 | 2500 | 2500 |  | 1700 | 1700 | 1700 | [5 empty] | (lf) | 1 | Plumbing
19 | Specialties and accessories | 0.2 | 75 | 100 | 100 | 5 | 75 | 100 | 100 | 5 | 75 | 100 | 100 | 5 | 50 | 75 | 75 | 5 | 5 | 5 | 5 | 0 | No. | 1 | Specialties
20 | Sprinkler Rough | 0.07 | 2120 | 2120 | 2120 |  | 1400 | 1400 | 1400 |  | 2120 | 2120 | 2120 |  | 1400 | 1400 | 1400 | [5 empty] | (lf) | 1 | Fire Sprinkler
21 | Tape and Finish | 0.007 | 36000 | 36000 | 36000 | 0 | 24000 | 24000 | 24000 |  | 36000 | 36000 | 36000 | 0 | 24000 | 24000 | 24000 | 0 | 8000 | 8000 | 8000 | 8000 | sq.ft. | 2 | Drywall
22 | T-Bar | 0.014 | 30000 | 30000 | 30000 | 0 | 20000 | 20000 | 20000 | 0 | 30000 | 30000 | 30000 | 0 | 20000 | 20000 | 20000 | 0 | 5000 | 5000 | 5000 | 0 | sq.ft. | 2 | Ceiling Tile
23 | Tele/data, Nurse Call, Security, AV, and Fire Alarm | 0.008 | 3000 | 3000 | 3000 |  | 2500 | 2500 | 2500 | 0 | 3000 | 3000 | 3000 | 0 | 2500 | 2500 | 2500 | 0 | 1000 | 1000 | 1000 | 0 | (lf) | 1 | Electrical
24 | TOP TRACK, BEAM CLAMPS ETC. | 0.25 | 1000 | 1000 | 1000 | 0 | 650 | 650 | 650 | 0 | 1000 | 1000 | 1000 | 0 | 650 | 650 | 650 | 0 |  |  |  | 1500 | (lf) | 2 | Drywall
25 | VAV and Low Pressure Ducts | 0.1 | 4000 | 4000 | 4000 |  | 2650 | 2650 | 2650 |  | 4000 | 4000 | 4000 |  | 2650 | 2650 | 2650 | [5 empty] | (lf) | 1 | Mechanical
26 | Wall, Hard Ceiling, and Soffit Framing | 0.04 | 1900 | 1900 | 1900 | 0 | 1300 | 1300 | 1300 | 0 | 1900 | 1900 | 1900 | 0 | 1300 | 1300 | 1300 | 0 |  |  |  | 3000 | sq.ft. | 2 | Drywall
27 | Wall, Hard Ceiling, and soffit MEP Roughins | 0.3 | 25 | 25 | 25 | 0 | 15 | 15 | 15 | 0 | 25 | 25 | 25 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 40 | No. | 1 | Mechanical
The maximum resources for each trade are as follows:
| Subcontractor | Maximum Resources
| Casework | 12
| Ceiling | 12
| Doors, Frames and Hardware | 4
| Drywall | 20
| Electrical | 12
| Fire Sprinkler | 3
| Fireproofing | 10
| Floor Coverings | 12
| Mechanical | 16
| Painting | 8
| Plumbing | 8
| Specialties | 1
Sequence of activities
Item
1 | TOP TRACK, BEAM CLAMPS ETC. (After structure completed in an area)
2 | Fireproofing (NOTE: Fireproofing on the third level can only start after roof has been completed in the same quadrant)
3 | Frame priority fullheight walls etc.
4 | Sprinkler Rough
5 | Medium pressure duct
6 | Mechanical Rough
7 | VAV and Low Pressure Ducts
8 | Dom Water
9 | Rain Water Leaders, Waste and Vent
11 | Branch conduit
12 | Feeder conduit
13 | Wall, Hard Ceiling, and Soffit Framing
14 | Wall, Hard Ceiling, and soffit MEP Roughins
15 | MED GAS
16 | Cable Tray
17 | Tele/data, Nurse Call, Security, AV, and Fire Alarm
18 | Drywall
19 | Tape and Finish
20 | Paint
21 | T-Bar
22 | Light Fixtures, Diffusers, Ceiling Mounted Trim
23 | Ceiling tile
24 | Casework, Millwork
25 | MEP Trim
26 | Floor coverings
27 | Specialties and accessories
28 | Doors & Hardware