## Slide 1: Exercise Session 11
Power systems

## Slide 2: Question 1
In an isolated neutral network there is a high-resistance 1-phase earth fault. The network’s earth capacitance is C0, voltage U and the fault resistance is Rf. Derive expressions for
earth fault current
neutral point voltage
faulty phase’s voltage
healthy phases’ voltage

## Slide 3: Question 1
Positive sequence network (positive sequence impedances small compared to the zero sequence network impedances):
Negative sequence network (negative sequence impedances small compared to the zero sequence network impedances):
Zero sequence network:
As we have learned previously (see E5Q3), in a single phase-to-earth fault,
the sequence networks are in series and the circuit is
closed by an impedance 3 times the fault impedance 
U1
U2
U0

## Slide 4: Question 1
Single phase-to-earth fault:
earth fault current
b) neutral point voltage (zero sequence voltage is the voltage between neutral and ground)

## Slide 5: Question 1
Single phase-to-earth fault:
Correspondingly:
с) faulty phase’s voltage
d) healthy phases’ voltage

## Slide 6: Question 2
Show that in an isolated neutral network, that has an earth capacitance c0 = 6.13 nF/km, the zero resistance earth fault current can be approximately expressed as:
, where [U] = 1 kV, [Ie] = 1 A, [l] = 1 km

## Slide 7: Question 2
Single phase-to-earth fault:
If
, then
If [U] = 1 kV and [l] = 1 km, then

## Slide 8: Question 3
Choose the smallest possible fuse to the transformer’s low-voltage side so that the protection is selective considering the IN = 35 A fuse. The two cases are:
1) l = 150 m, xj = 0.075 /km, rj = 0.103 /km
2) l = 600 m, xj = 0.104 /km, rj = 0.868 /km
Selectivity can be considered sufficient when the major fuse’s melting time is at least ten times the melting time of the minor fuse plus the maximum arcing time (10 ms). When we have short melting times (t<1 ms), fusing is selective enough when the major fuse’s melting energy I2tS is at least three times the minor fuse’s operation energy I2ta. The melting times and energies are presented in the following pictures.
major
minor

## Slide 9: Question 3
Choose the smallest possible fuse to the transformer’s low-voltage side so that the protection is selective considering the IN = 35 A fuse. The two cases are:
1) l = 150 m, xj = 0.075 /km, rj = 0.103 /km
2) l = 600 m, xj = 0.104 /km, rj = 0.868 /km
Selectivity can be considered sufficient when the major fuse’s melting time is at least ten times the melting time of the minor fuse plus the maximum arcing time (10 ms). When we have short melting times (t<1 ms), fusing is selective enough when the major fuse’s melting energy I2tS is at least three times the minor fuse’s operation energy I2ta. The melting times and energies are presented in the following pictures.
major
minor
If t>10ms:
If t<1 ms:

## Slide 10: Question 3
Melting times of fuses with different nominal current as a function of current.
I2tS melting energy, I2ta operation energy, melting time is less than 1 ms.

## Slide 11: Question 3
The worst case from the selectivity point of view is when a short circuit happens at the 35-A fuse terminals. Let us compute the 3-phase short circuit current in this point:
Assuming that the voltage is at its rated value.
In 400-V voltage level, transformer parameters:

## Slide 12: Question 3: Part 1
The major fuse size
From figures shown on the previous slide: the operation time of a 35-A fuse with the short circuit current fuse melting time corresponds to a value below 1 ms, therefore, we use the melting/operating energy diagram. From the second diagram the 35-A fuse corresponds to a operating energy value of at 220 V. According to our initial selectivity criteria (if t<1ms),
the
On the diagram the next fuse that satisfies this condition is a 100 A fuse.
Short circuit current:
Line characteristics:

## Slide 13: Question 3
Melting times of fuses with different nominal current as a function of current.
I2tS melting energy, I2ta operation energy, melting time is less than 1 ms.

## Slide 14: Question 3: Part 2
The major fuse size
From figures shown on the previous slide: the operation time of a 35-A fuse with the short circuit current fuse melting time corresponds to a value 20 – 30 ms. Therefore, we use the same diagram. According to our initial selectivity criteria (if t >10 ms ),
the On the diagram, the next fuse that satisfies this condition is a 63-A fuse.
Short circuit current:
Line characteristics:

## Slide 15: Question 3
Melting times of fuses with different nominal current as a function of current.