## Slide 1: Exercise 9
Power systems

## Slide 2: Question 1
A two-phase zero-impedance fault occurs at point A. The distance between phases in the bus bar system is 2.5 m. Calculate the maximum peak force affecting each phase (per length) in area 1. Apply the IEC recommended voltage correction factor (C factor) to calculate the maximum short circuit current.
G: X’’d = X2 = 15 , X0 = 10 
M: Zk = 10 
Line: X1j = 5 , X0j = 16 
http://help.easypower.com/ezp/9.6/content/06_IEC_Short_Circuit/Setting_the_Short_Circuit_Method.htm

## Slide 3: Question 1
US = UT
(Zf = 0)
Zero
Positive
Negative
Zf

## Slide 4: Question 1
We can see that the voltages of the
positive and negative sequence are the same and
the currents are of the same magnitude but in different directions
 We get the following equivalent circuit:
Zf
Z2
Z1
E1
U1
U2
I1
I2

## Slide 5: Question 1 Maximum peak force
Positive sequence network:
G: X’’d = X2 = 15 , X0 = 10 
M: Zk = 10 
Line: X1j = 5 , X0j = 16 

## Slide 6: Question 1 Maximum peak force
Positive sequence network:
G: X’’d = X2 = 15 , X0 = 10 
M: Zk = 10 
Line: X1j = 5 , X0j = 16 
http://help.easypower.com/ezp/9.6/content/06_IEC_Short_Circuit/Setting_the_Short_Circuit_Method.htm

## Slide 7: Question 1 Maximum peak force
Negative sequence network:
G: X’’d = X2 = 15 , X0 = 10 
M: Zk = 10 
Line: X1j = 5 , X0j = 16 

## Slide 8: Question 1 Maximum peak force
Two phase short circuit ( I1 = -I2 ):

## Slide 9: Question 1 Maximum peak force
Peak value of the alternating current:
In addition, there is a DC-component. If no attenuation, the amplitude of DC-component can be equal to the peak value of the alternating current component.
2
1.8 (used in real
high-voltage
systems
which have
losses,
see lecture 9)

## Slide 10: Question 1 Maximum peak force
Max force is between lines S and T:

## Slide 11: Question 2
A short circuit occurs in a 24-kV bus bar system. The phase current instantaneous values are iR = 30 kA, iS = 15 kA and iT = 15 kA.
a = 0.3 m
Calculate the forces (per length) that affect each bus bar for the
Upper system
Lower system
a)
b)

## Slide 12: Question 2 a) forces per length in the upper system
iR= 30 kA, iS=15 kA and iT=15 kA.
a = 0.3 m

## Slide 13: Question 2 a) forces per length in the upper system
a=0.3 m

## Slide 14: Question 2 b) forces per length in the lower system
iR= 30 kA, iS=15 kA and iT=15 kA.
a
a
a
a=0.3 m
a
a
a
60 deg.
Ref = 0 deg
-30deg.

## Slide 15: Question 2 b) forces per length in the lower system
a
a
a
Directly up
Directly down
Directly down
210deg.
90deg.
Ref = 0 deg

## Slide 16: Question 3
Two identical transformers each have a nominal or no-load ratio of 33/11 kV and a reactance of 2  referred to the 11-kV side; resistance may be neglected. The transformers operate in parallel and supply a load of 9 MVA, 0.8 p.f. lagging. Calculate the current taken by each transformer when they operate five tap steps apart (each step is 1.25 per cent of the nominal voltage).

## Slide 17: Question 3 Current by each transformer
Let’s select load side as a base reference:
Transformer reactance in per unit:
LOAD
33/
11kV
S = 9 MVA, cos φ = 0.8ind
Grid
Load current in per unit:
A
B

## Slide 18: Question 3 Current by each transformer
U1
U2
Ta
Tb
ΔU
+
-
-
+
-
+
Icirc
Equivalent circuit
An approximate solution is to use this equivalent circuit, where ΔU is the regulating transformer to accommodate the voltage tap change in the second transformer. This voltage creates a circulating current Icirc .
With switch S closed, only a very small fraction of that current goes through the load impedance, because it is much larger than the transformers impedance, then superposition principle is applied to ΔU and the source voltage. With ΔU short-circuited, the current in each path is half the load current. Then we just need to superimpose the circulating current.
S

## Slide 19: Question 3 Current by each transformer, when 5 voltage taps of 1.25%
Voltage difference due to tap setting creates a current circulating through
the parallel transformers:
XtA
LOAD
XtB
Grid
iL
iL
iL/2+icirc
iL/2-icirc

## Slide 20: Question 4
Three 11-kV, 100-MVA generators are
connected to common busbars. Each is
connected via a 100-MVA inductor and an
identical circuit breaker. The inductors
have reactances of 0.15pu, 0.20pu and 0.30pu.
If the generators each have a transient
reactance of 0.25pu, what is the minimum
circuit-breaker rating to protect the generators against a
fault on the common busbars?

## Slide 21: Question 4
G1:
G2:
G3:
Therefore, the minimum circuit-breaker rating to protect the generators from common busbar fault, since they were said to be all identical, is 250 MVA.
Inductor reactances 0.15pu, 0.20pu and 0.30pu.
100-MVA generators each have a transient
reactance of 0.25pu
G
L
G
G
L
L
breaker
breaker
breaker
Grid
common bus