## Slide 1
Connection of Storage Devices to Electrical Energy Chains
Floran Martin, Jarno Kukkola,
Annukka Santasalo-Arnio, Sandra Correa Gonzalez
AAE – E3070 – Electrical Energy Storage System L
Spring 2020

## Slide 2
Today, you can learn :
Where the electrical storage system are commonly located
One pre-design method applied for an hydraulic storage system
How to select the components for converting different types of energy

## Slide 3
Power Plants
Electric Grid
Consumers
Nuclear Power Plants
Natural Gas Generators
Wind Farms
Photovoltaic Farms
Hydropower Plants
Transmission Lines
Utility scale storage
Plug-in Electric Vehicles
Photovoltaic
Distributed Substations
Distributed storage
Shaving storage
Smoothing storage

## Slide 4
Production
10
8
6
4
2
0
1 day
Nuclear
Wind
Farm
Power Production [GW]
Consumption
65
60
55
50
45
55
50
45
40
35
M
M
Tu
Tu
W
W
F
F
Th
Th
Sa
Sa
Su
Su
Power Consumption [GW]
Winter
Summer
1 day
Supply the consumer need
Drop the number of power plants

## Slide 5
Hydropower Storage System
High reservoir
Low reservoir
Pump / Turbine
Motor / Generator
Electric Grid
MECH
ELEC
Water of mass m [kg]
Altitude h [m]
Hydraulic Energy Stored [J]:
Gravitation constant g = 9,819 m/s2
Power developed [W]:
Electric Power [W]:
Efficiency of the chain:
Generator mode

## Slide 6
Hydropower Storage System
Potential Energy
Kinetic Energy
Translation Mechanical
Rotation
Mechanical
AC Electrical
Electric
Network
Rotation
Mechanical
Var. Freq. AC Electrical
Adjusted
AC Electrical
Hydropower plant
Pump/Turbine
Motor/Generator
Frequency Converter
Force
Torque
Voltage
Voltage
Speed
Rot. Speed
Current
Current

## Slide 7
Design a Hydropower Storage System
Geographic Location :
65
60
55
50
45
M
Tu
W
F
Th
Sa
Su
Winter
Consumption profile [GW]
Production source
Power plant produces constantly 55 GW
Environmental respect
Assumption
The level of the water is negligible compared with the altitude of the reservoir.
The consumption profile can be exceptionally considered sinusoidal
The overall chain efficiency is 65 %
65
60
55
50
45
M
Tu
W
F
Th
Sa
Su

## Slide 8
Design a Hydropower Storage System
Period: T = 24 hours
Electrical Energy to stored:
Step 1 – Determine the Stored Energy from the Consumption Side
Consumed Electrical power [GW]:
Eelec = 275 TJ = 76,4 GWh
65
60
55
50
45
M
Tu
W
F
Th
Sa
Su
Motor
Generator
Electrical power to deliver and store [GW]:

## Slide 9
Design a Hydropower Storage System
Hydraulic Energy :
Mass of water :
46 000 Olympic swimming pools (3m depth)
Turbine/Pump
Motor/Generator
Power Converter
Step 2 – Determine the Stored Energy from the Production Side
m = 172 Gkg = 172 Mt
Ehydro = 423 TJ = 117 GWh

## Slide 10
Design a Hydropower Storage System
Hydraulic power + Power plant power
Electric power
Power plant power
65
60
55
50
45
40
70
Power [GW]
M
Tu
W
F
Th
Sa
Su
Mass Flow of water :
Hydraulic Power :
Empty 1,67 olympic swimming pools every second
Step 3 – Evaluate intrinsec quantities of the storage system

## Slide 11
Design a Hydropower Storage System
Step 4 – Design the components of the energy chain
Hydropower plant
Pump/Turbine
Motor/Generator
Frequency Converter
Force
Torque
Voltage
Voltage
Speed
Rot. Speed
Current
Current
Ehydro = 423 TJ
Eelec = 275 TJ
Phydro = 15,4 GW
Pelec = 10 GW
How many turbines do we need ?
What is the power of the motor/gen. ?
.... ?
.... ?
Qhydro = 6 279 m3/s
felec = 50 Hz
Velec = 10 kV

## Slide 12
Design a Hydropower Storage System
Step 4 – Design the components of the energy chain
Pumps/Turbines (Analyze different solutions)
  77 pumps/turbines of 200 MW at 500 rpm (Alstom Hydro)
Force
Torque
Speed
Rot. Speed
Qturbine = Qhydro /77 =81,5 m3/s
ηturbine = 87 %
Max Flow of water :
Rated Efficiency :
Phydro = 15,4 GW
Protation = 13,4 GW
Ploss = 2 GW

## Slide 13
Design a Hydropower Storage System
Step 4 – Design the components of the energy chain
Torque
Voltage
Rot. Speed
Current
Protation = 13,4 GW
Ploss = 0,2 GW
Pgenerator = 13,2 GW
Motors/Generators (Analyze different solutions)
  77 Induction Motor of 174 MW at 500 rpm (Alstom Hydro)
ηgenerator = 98,5 %
Rated Efficiency :
Maximum current :
Igenerator = 8,3 kA per generator

## Slide 14
Design a Hydropower Storage System
Step 4 – Design the components of the energy chain
Voltage
Voltage
Current
Current
Pgenerator = 13,2 GW
Ploss = 0,4 GW
Pelec = 12,8 GW
Frequency Converters (Analyze different solutions)
  77 Voltage Source Inverters of 172 MW for 50 Hz (ABB Drive)
ηconverter = 97 %
Rated Efficiency :
Output current :
Ielec = 16,6 kA per converter

## Slide 15
Design a Hydropower Storage System
Step 5 – Estimate the performance of the storage system
Phydro = 15,4 GW
Pelec = 12,8 GW
Ploss = 2,6 GW
ηchain = 83 %
The round trip efficiency considers the conversion chain for storing and for returning the energy.
Phydro
Pelec
Pelec
ηstoring = 83 %
ηreturing = 83 %
η = 69 %
ηround trip = ηstoring ηreturning

## Slide 16
Design a Hydropower Storage System
Would we get a higher efficiency with less turbines ?
What is the autonomy of our storing system if one power plant is shut down ?
Our initial guess of the efficiency is lower than the designed efficiency
Step 6 – Adjust and improve the design: Back to step 1
The competitors could have cheaper solution, should we check it ?