## Slide 1: Exercise 8
Power systems

## Slide 2: Question 1
The generator is feeding the network. P=250 MW and Q=0 Mvar. Calculate the generator terminal voltage when it is disconnected from the network.

## Slide 3: Question 1
Generated voltage equals to receiving end voltage (U) + voltage drop across the reactance.
Calculating reactance values on the side of the 20-kV Transformer
When disconnected from the network, the terminal voltage Ug of the generator rises to the value of E generated

## Slide 4: Question 1
Generator voltage and terminal voltage at the time of disconnection:
Converting further:

## Slide 5: Question 2
A highly capacitive circuit of capacitance per phase 100 F is disconnected by a circuit breaker, the source inductance being 1 mH. The breaker gap breaks down when the voltage across it reaches twice the system peak line-to-neutral voltage of 38 kV. Calculate the current flowing with the breakdown and its frequency and compare it with the normal (50-Hz) charging current of the circuit.

## Slide 6: Question 2
Energy is distributed half into the electric field and half in the magnetic field: Inductive energy equals to capacitive energy during a travelling wave.
The breaker gap breaks down, when the voltage across it reaches twice the system peak line-to-neutral voltage of 38 kV
At this moment, the electricity starts to
“travel”, and thus we can convert
the voltage into current:
Electric Power Systems, 5th ed., Weedy et al.

## Slide 7: Question 2
Frequency:
The normal charging current of the circuit is:

## Slide 8: Question 3
The effective inductance and capacitance of a faulted system as viewed by the contacts of a circuit breaker are 2 mH and 500 pF, respectively. The circuit breaker chops the fault current when it has an instantaneous value of 100 A. Calculate the restriking voltage set up across the circuit breaker. Neglect resistance.

## Slide 9: Question 3
The breaker tends to open the circuit before the current natural-zero, and the electromagnetic energy present is rapidly converted to electrostatic energy

And the restriking voltage
(in addition to the system voltage) is
Where
and
is the value of the current at the
instant of chopping (t=0).
Electric Power Systems, 5th ed., Weedy et al.

## Slide 10: Question 3
This is the overvoltage transient that oscillates in the disconnected system
behind the opened circuit breaker. The stress over the breaker is the difference
of this voltage and power system voltage at the breaker terminals.

## Slide 11: Question 4
A long overhead line has a surge impedance of 500 and an effective resistance at the frequency of the surge of 7/km. If a surge of magnitude 500kV enters the line at a certain point, calculate the magnitude of this surge after it has traversed 100km and calculate the resistive power loss of the wave over this distance. The wave velocity is 3x105km/s.

## Slide 12: Question 4
Considering the power losses (dp) over a length (dx), where resistance and shunt are R(Ω) and G( )
Therefore, power loss dp:
Electric Power Systems, 5th ed., Weedy et al.

## Slide 13: Question 4
Calculating magnitude of a surge at x=100 km
Calculating resistive power loss: