## Daily monitoring results
Please enter the daily process monitoring results here and the results from your group's post-treatment analysis on the Post-treatment results sheet
Day |  | Wed | Thu | Fri | Mon | Tue
Date |  | 23.1.19 | 24.1.19 | 25.1.19 | 28.1.19 | 29.1.19
pH meter reading |  | 4.7 | 4.9 | 4.6 | 5 | 5.1
pH | Influent | 7.67 | 7.27 | 7.96 | 7.26 | 7.51
| After sedimentation | 4.32 | 4.47 | 4.13 | 4.6 | 4.9
| Effluent | 4.47 | 4.59 | 4.1 | 4.84 | 4.93
UV-254 absorbance | Influent | 0.443 | 0.453 | 0.445 | 0.449 | 0.448
| After sedimentation | 0.137 | 0.157 | 0.064 | 0.11 | 0.238
| Effluent | 0.148 | 0.171 | 0.07 | 0.08 | 0.246
Turbidity, NFU | Influent | 6.7 | 6 | 5.3 | 5 | 5.6
| After sedimentation | 6.1 | 6.9 | 5.1 | 7.4 | 7.4
| Effluent | 4.3 | 5.4 | 2.9 | 3.7 | 6.6
Alkalinity, mmol/l | After sedimentation | - | 0 | - | - | -
| Effluent | - | 0.0124 | - | - | -
Fe concentration, μg/l | Raw water | - | - | - | - | 229.8
| After sedimentation | - | - | - | - | 1953.1
| Effluent | - | - | - | - | 1200.1
Notes |  | Record here the adjustments you made to the pilot, observations etc.
|  | mixing rate adjusted from 9V to 6V due to flocs being destroyed. all necessary analysis and work (sludge removal+filter backwash) was carried out. influent flowrate balanced to 100ml/min. | rotating speed increased from 6V --> 7V, more flocs are produced but they are sedimenting by the mixing chambers, turbidity really high, higher than on previous day /KN & MH | Today, I did all the compulsory measurements, cleared the sludge, backwashed the filter and increased 5 liters of PIX solution to the canister, so that it suffices for the weekend. Additionally, we tried to clean the sludge from the flocculation basin. I increased the mixing to 20 V for 25 minutes. The sludge began moving to the sedimentation basin. The mixing was turned down to 7 V. I increased also PIX dosing to 2,6 ml/min, corresponding a factor of 1.2. | all necessary analysis done, a lot of sludge formed over the weekend so it took time to clear out. no changes were made as iron analysis samples were prepared for analysis on Tuesday. There were air bubbles in the sludge outlet tank (below the table). We figured this could be due to oxygen content in raw water. | still not so proper flocs formation (too much Iron in the effluent); new raw water prepared, KMnO4 value- 8,8 mg/l; sandfilter backwashed, level 15,5; iron measurements taken before any adjustments (results above), adjusted flow rate of influent (changed to 100 ml/min from 115), PIX rate of 2,3 ml/min remained the same (the dosage per volume increased then, since the flow of influent rate decreased)