## Project Overview
Project overview
Sumo version: | 19
Model: | Sumo1
Scenario: | Default scenario
Model Options: | 1-step nitrification/denitrification
Input gas phase concentrations
Skip pH calculations
Simulation from: | Hot start
Stop time: | 14 | days
Data interval: | 15 | minutes

## Modified Parameters
Modified parameters
Influent - Influent specifications
Symbol | Name | Value | Unit | Comment
Q | Flow rate | 18446 | m3/d
TCOD | Total COD | 381 | g COD/m3
TKN | Total Kjeldahl nitrogen | 54 | g N/m3
TP | Total phosphorus | 8 | g P/m3
Influent - Influent fractions
Symbol | Name | Value | Unit | Comment
frSCCOD,TCOD | Fraction of filtered COD (SCCOD, 1.5 µm, incl. colloids) in total COD | 44.6 | %
frSCOD,TCOD | Fraction of flocculated filtered (SCOD, wo colloids) COD in total COD | 22.3 | %
CSTR5 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1333 | m3
htank | Tank depth | 4 | m
CSTR5 - Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 15000 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 1
CSTR4 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1333 | m3
htank | Tank depth | 4 | m
CSTR4 - Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 50000 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 1
CSTR3 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1333 | m3
htank | Tank depth | 4 | m
CSTR3 - Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 50000 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 1
CSTR2 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1000 | m3
htank | Tank depth | 4 | m
CSTR2 - Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 0 | Nm3 gas.d-1
CSTR1 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1000 | m3
htank | Tank depth | 4 | m
CSTR1 - Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 0 | Nm3 gas.d-1
Clarifier - Clarifier settings
Symbol | Name | Value | Unit | Comment
A | Surface area | 1500 | m2
haverage | Depth | 4 | m
Qsludge,target | Sludge flow | 18831 | m3/d
Clarifier - Settling parameters
Symbol | Name | Value | Unit | Comment
vmax | Maximum Vesilind settling velocity | 474 | m/d
rhin | Coefficient for hindered settling | 0.576 | L/g
rfloc | Coefficient for flocculent settling | 2.86 | L/g
fns | Fraction of non-settleable solids | 0.228 | %
Clarifier - Layer number
Symbol | Name | Value | Unit | Comment
n | Number of layers | 10
External - Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 385 | m3/d
Internal - Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 55338 | m3/d

## State Var. at Steady state
State variables
Symbol | Influent | CSTR1 | CSTR2 | CSTR3 | CSTR4 | CSTR5 | Unit
Volatile fatty acids (VFA) | 19.4245 | 0.020956 | 0.00012627 | 4.7863e-07 | 1.1844e-08 | 1.3731e-08 | g COD/m3
Readily biodegradable substrate (non-VFA) | 43.705 | 1.6827 | 0.8307 | 1.063 | 1.0099 | 0.96253 | g COD/m3
Methanol (MEOL) | 1e-40 | 1e-50 | 1e-50 | 1e-50 | 1e-50 | 1e-50 | g COD/m3
Colloidal biodegradable substrate | 66.0431 | 0.021797 | 3.9199e-05 | 5.2908e-08 | 7.1412e-11 | 9.6384e-14 | g COD/m3
Slowly biodegradable substrate | 130.4497 | 87.2828 | 82.9491 | 73.1735 | 64.7228 | 57.5794 | g COD/m3
Soluble unbiodegradable organics | 19.4245 | 19.4245 | 19.4245 | 19.4245 | 19.4246 | 19.4246 | g COD/m3
Colloidal unbiodegradable organics | 16.5108 | 0.005391 | 9.695e-06 | 1.3086e-08 | 1.7662e-11 | 2.3839e-14 | g COD/m3
Particulate unbiodegradable organics | 51.8276 | 1433.7604 | 1433.7688 | 1433.7735 | 1433.7778 | 1433.7812 | g COD/m3
Stored polyhydroxyalkanoates (PHA) | 1e-40 | 9.561e-10 | 8.475e-10 | 6.9597e-10 | 5.7192e-10 | 4.721e-10 | g COD/m3
Stored glycogen (GLY) | 1e-40 | 0.00043735 | 0.0004034 | 0.00031375 | 0.00024319 | 0.00019003 | g COD/m3
Endogenous decay products | 3.702 | 511.9126 | 512.2805 | 513.271 | 514.267 | 515.2594 | g COD/m3
Anaerobic endogenous decay products | 1e-40 | 0.00044922 | 0.00077297 | 0.0004942 | 0.0003144 | 0.00020295 | g COD/m3
Ordinary heterotrophs (OHO) | 18.5099 | 1402.9803 | 1403.4185 | 1405.0555 | 1405.9306 | 1405.6767 | g COD/m3
Phosphorus accumulating organisms (PAO) | 0.1 | 1.5415 | 1.5411 | 1.5399 | 1.5387 | 1.5372 | g COD/m3
Glycogen accumulating organisms (GAO) | 0.1 | 1.5684 | 1.5679 | 1.5669 | 1.5657 | 1.5642 | g COD/m3
Anoxic methanol utilizers (MEOLO) | 0.1 | 1.5415 | 1.5411 | 1.5399 | 1.5387 | 1.5372 | g COD/m3
Aerobic nitrifying organisms (NITO) | 0.1 | 103.5168 | 103.4248 | 104.1807 | 104.5207 | 104.4594 | g COD/m3
Acidoclastic methanogens (AMETO) | 0.1 | 0.70689 | 0.70567 | 0.70258 | 0.69945 | 0.69622 | g COD/m3
Hydrogenotrophic methanogens (HMETO) | 0.1 | 0.22879 | 0.22711 | 0.22286 | 0.21867 | 0.21453 | g COD/m3
Total ammonia (NHx) | 36.4709 | 6.5662 | 6.8923 | 2.8147 | 0.59048 | 0.14209 | g N/m3
Nitrate and nitrite (NOx) | 1e-40 | 12.9078 | 11.4012 | 15.5415 | 18.0028 | 18.7835 | g N/m3
Dissolved nitrogen (N2) | 16 | 19.3568 | 20.3962 | 17.8629 | 17.3051 | 17.186 | g N/m3
Soluble biodegradable organic N (from SB) | 1.7482 | 1.0311 | 0.86715 | 1.0582 | 1.1196 | 1.1163 | g N/m3
Particulate biodegradable organic N (from XB) | 8.8601 | 5.3883 | 5.155 | 4.6199 | 4.149 | 3.744 | g N/m3
Particulate unbiodegradable organic N | 0.51828 | 14.3449 | 14.345 | 14.345 | 14.3451 | 14.3451 | g N/m3
Orthophosphate (PO4) | 4.6512 | 5.6034 | 5.6467 | 5.6783 | 5.7349 | 5.8118 | g P/m3
Stored polyphosphate (PP) | 1e-40 | 3.3398e-08 | 3.3488e-08 | 3.3652e-08 | 3.3793e-08 | 3.3912e-08 | g P/m3
Soluble biodegradable organic P (from SB) | 0.43705 | 0.028607 | 0.018088 | 0.030306 | 0.030543 | 0.029547 | g P/m3
Particulate biodegradable organic P (from XB) | 1.9521 | 1.3386 | 1.2918 | 1.1806 | 1.0798 | 0.99058 | g P/m3
Particulate unbiodegradable organic P | 0.051828 | 2.8193 | 2.8194 | 2.8194 | 2.8194 | 2.8194 | g P/m3
Dissolved oxygen (O2) | 1e-40 | 0.012443 | 0.0017199 | 2.4616 | 4.4331 | 2.8924 | g O2/m3
Dissolved methane (CH4) | 1e-40 | 0.0052107 | 0.0044113 | 0.0068456 | 0.007408 | 0.0075381 | g COD/m3
Dissolved hydrogen (H2) | 1e-40 | 0.12112 | 0.090498 | 0.18232 | 0.19586 | 0.19785 | g COD/m3
Total inorganic carbon (CO2) | 90 | 98.8033 | 112.2323 | 97.5586 | 88.1692 | 82.2198 | g TIC/m3
Inorganics in influent and biomass | 22.9001 | 608.7888 | 608.8282 | 609.0936 | 609.2369 | 609.2417 | g TSS/m3
Other strong cations (as Na+) | 109.9 | 107.6583 | 107.6433 | 107.5395 | 107.4836 | 107.4823 | g Na/m3
Other strong anions (as Cl-) | 300 | 296.5432 | 296.5201 | 296.3599 | 296.2739 | 296.2718 | g Cl/m3
Calcium | 150 | 150 | 150 | 150 | 150 | 150 | g Ca/m3
Magnesium | 15 | 15 | 15 | 15 | 15 | 15 | g Mg/m3
Potassium | 16 | 16 | 16 | 16 | 16 | 16 | g K/m3
Ferrous ion (Fe2) | 1e-40 | 1.0365e-16 | 1e-50 | 6.7075e-17 | 1e-50 | 4.5667e-17 | g Fe/m3
Active hydrous ferric oxide, high surface (HFO,H) | 9.0426e-41 | 1.1456e-16 | 1e-50 | 1e-50 | 1.4385e-18 | 1e-50 | g Fe/m3
Active hydrous ferric oxide, low surface (HFO,L) | 9.5745e-42 | 9.5173e-15 | 1.0314e-14 | 8.927e-15 | 8.6064e-15 | 9.351e-15 | g Fe/m3
Aged unused hydrous ferric oxide (HFO,old) | 1e-40 | 5.3096e-08 | 5.3156e-08 | 5.3237e-08 | 5.3317e-08 | 5.3397e-08 | g Fe/m3
P-bound hydrous ferric oxide, high surface (HFO,H,P) | 1e-40 | 2.9349e-16 | 8.7598e-16 | 3.9851e-16 | 4.0286e-16 | 6.2017e-16 | g Fe/m3
P-bound hydrous ferric oxide, low surface (HFO,L,P) | 1e-40 | 2.2898e-13 | 2.2956e-13 | 2.3048e-13 | 2.3136e-13 | 2.3116e-13 | g Fe/m3
Aged used hydrous ferric oxide, high surface (HFO,H,P,old) | 1e-40 | 4.917e-08 | 4.9225e-08 | 4.9299e-08 | 4.9374e-08 | 4.9448e-08 | g Fe/m3
Aged used hydrous ferric oxide, low surface (HFO,L,P,old) | 1e-40 | 8.8653e-08 | 8.8753e-08 | 8.8887e-08 | 8.9021e-08 | 8.9155e-08 | g Fe/m3
Aluminium hydroxide compounds (AlOH) | 1e-40 | 1.4007e-09 | 1.4055e-09 | 1.4084e-09 | 1.4069e-09 | 1.4009e-09 | g Al/m3
Aluminium phosphate compounds (AlP) | 1e-40 | 6.6554e-08 | 6.6626e-08 | 6.6725e-08 | 6.683e-08 | 6.6939e-08 | g Al/m3
Calcium carbonate (CaCO3) | 1e-40 | 4.9221e-08 | 4.9277e-08 | 4.9351e-08 | 4.9426e-08 | 4.95e-08 | g TSS/m3
Amorphous calcium phosphate (ACP) | 1e-40 | 4.9245e-08 | 4.9301e-08 | 4.9375e-08 | 4.945e-08 | 4.9524e-08 | g TSS/m3
Struvite (STR) | 1e-40 | 4.9183e-08 | 4.9238e-08 | 4.9313e-08 | 4.9387e-08 | 4.9461e-08 | g TSS/m3
Vivianite (Vivi) | 1e-40 | 4.962e-08 | 4.9676e-08 | 4.9751e-08 | 4.9826e-08 | 4.9902e-08 | g TSS/m3
Enthalpy | 83626 | 83626.3161 | 83626.3206 | 83626.329 | 83626.3404 | 83626.3526 | kJ.m-3
Carbon dioxide gas (CO2) off-gas concentration |  | 0.11359 | 0.11359 | 0.054 | 0.054 | 0.054 | g TIC/m3
Methane gas (CH4) off-gas concentration |  | 1e-40 | 1e-40 | 0.001 | 0.001 | 0.001 | g COD/m3
Hydrogen gas (H2) off-gas concentration |  | 1e-40 | 1e-40 | 0.05 | 0.05 | 0.05 | g COD/m3
Oxygen gas (O2) off-gas concentration |  | 1e-40 | 1e-40 | 1.3 | 1.3 | 1.3 | g O2/m3
Ammonia gas (NH3) off-gas concentration |  | 1e-40 | 1e-40 | 1e-40 | 1e-40 | 1e-40 | g N/m3
Nitrogen gas (N2) off-gas concentration |  | 1.3734 | 1.3734 | 4.9 | 4.9 | 4.9 | g N/m3

## Important Var. at steady state
Important variables
Symbol | Influent | CSTR1 | CSTR2 | CSTR3 | CSTR4 | CSTR5 | Effluent | Unit
Total suspended solids (TSS) | 151.3042 | 3185.5225 | 3183.6608 | 3180.8736 | 3177.8748 | 3174.3821 | 13.8997 | g TSS/m3
Total nitrogen | 52.2749 | 177.771 | 176.2385 | 176.1833 | 176.1551 | 176.1158 | 21.6922 | g N/m3
Nitrate and nitrite (NOx) | 1e-40 | 12.9078 | 11.4012 | 15.5415 | 18.0028 | 18.7835 | 18.7835 | g N/m3
Total ammonia (NHx) | 36.4709 | 6.5662 | 6.8923 | 2.8147 | 0.59048 | 0.14209 | 0.14209 | g N/m3
Total phosphorus | 8 | 50.3089 | 50.3089 | 50.309 | 50.309 | 50.3091 | 6.0748 | g P/m3
Total COD | 370.197 | 3566.1963 | 3561.6812 | 3555.5146 | 3549.2151 | 3542.693 | 35.8103 | g COD/m3
Dissolved oxygen (O2) | 1e-40 | 0.012443 | 0.0017199 | 2.4616 | 4.4331 | 2.8924 | 2.8924 | g O2/m3

## Dry Influent
Influent
Time | Flow rate | Total COD | Total Kjeldahl nitrogen (TKN
d | m3/d | g COD/m3 | g N/m3
0 | 18446 | 381.19 | 54.4256
0.010417 | 18446 | 381.19 | 54.4256
0.020833 | 18446 | 381.19 | 54.4256
0.03125 | 18446 | 381.19 | 54.4256
0.041667 | 18446 | 381.19 | 54.4256
0.052083 | 18446 | 381.19 | 54.4256
0.0625 | 18446 | 381.19 | 54.4256
0.072917 | 18446 | 381.19 | 54.4256
0.083333 | 18446 | 381.19 | 54.4256
0.09375 | 18446 | 381.19 | 54.4256
0.10417 | 18446 | 381.19 | 54.4256
0.11458 | 18446 | 381.19 | 54.4256
0.125 | 18446 | 381.19 | 54.4256
0.13542 | 18446 | 381.19 | 54.4256
0.14583 | 18446 | 381.19 | 54.4256
0.15625 | 18446 | 381.19 | 54.4256
0.16667 | 18446 | 381.19 | 54.4256
0.17708 | 18446 | 381.19 | 54.4256
0.1875 | 18446 | 381.19 | 54.4256
0.19792 | 18446 | 381.19 | 54.4256
0.20833 | 18446 | 381.19 | 54.4256
0.21875 | 18446 | 381.19 | 54.4256
0.22917 | 18446 | 381.19 | 54.4256
0.23958 | 18446 | 381.19 | 54.4256
0.25 | 18446 | 381.19 | 54.4256
0.26042 | 18446 | 381.19 | 54.4256
0.27083 | 18446 | 381.19 | 54.4256
0.28125 | 18446 | 381.19 | 54.4256
0.29167 | 18446 | 381.19 | 54.4256
0.30208 | 18446 | 381.19 | 54.4256
0.3125 | 18446 | 381.19 | 54.4256
0.32292 | 18446 | 381.19 | 54.4256
0.33333 | 18446 | 381.19 | 54.4256
0.34375 | 18446 | 381.19 | 54.4256
0.35417 | 18446 | 381.19 | 54.4256
0.36458 | 18446 | 381.19 | 54.4256
0.375 | 18446 | 381.19 | 54.4256
0.38542 | 18446 | 381.19 | 54.4256
0.39583 | 18446 | 381.19 | 54.4256
0.40625 | 18446 | 381.19 | 54.4256
0.41667 | 18446 | 381.19 | 54.4256
0.42708 | 18446 | 381.19 | 54.4256
0.4375 | 18446 | 381.19 | 54.4256
0.44792 | 18446 | 381.19 | 54.4256
0.45833 | 18446 | 381.19 | 54.4256
0.46875 | 18446 | 381.19 | 54.4256
0.47917 | 18446 | 381.19 | 54.4256
0.48958 | 18446 | 381.19 | 54.4256
0.5 | 18446 | 381.19 | 54.4256
0.51042 | 18446 | 381.19 | 54.4256
0.52083 | 18446 | 381.19 | 54.4256
0.53125 | 18446 | 381.19 | 54.4256
0.54167 | 18446 | 381.19 | 54.4256
0.55208 | 18446 | 381.19 | 54.4256
0.5625 | 18446 | 381.19 | 54.4256
0.57292 | 18446 | 381.19 | 54.4256
0.58333 | 18446 | 381.19 | 54.4256
0.59375 | 18446 | 381.19 | 54.4256
0.60417 | 18446 | 381.19 | 54.4256
0.61458 | 18446 | 381.19 | 54.4256
0.625 | 18446 | 381.19 | 54.4256
0.63542 | 18446 | 381.19 | 54.4256
0.64583 | 18446 | 381.19 | 54.4256
0.65625 | 18446 | 381.19 | 54.4256
0.66667 | 18446 | 381.19 | 54.4256
0.67708 | 18446 | 381.19 | 54.4256
0.6875 | 18446 | 381.19 | 54.4256
0.69792 | 18446 | 381.19 | 54.4256
0.70833 | 18446 | 381.19 | 54.4256
0.71875 | 18446 | 381.19 | 54.4256
0.72917 | 18446 | 381.19 | 54.4256
0.73958 | 18446 | 381.19 | 54.4256
0.75 | 18446 | 381.19 | 54.4256
0.76042 | 18446 | 381.19 | 54.4256
0.77083 | 18446 | 381.19 | 54.4256
0.78125 | 18446 | 381.19 | 54.4256
0.79167 | 18446 | 381.19 | 54.4256
0.80208 | 18446 | 381.19 | 54.4256
0.8125 | 18446 | 381.19 | 54.4256
0.82292 | 18446 | 381.19 | 54.4256
0.83333 | 18446 | 381.19 | 54.4256
0.84375 | 18446 | 381.19 | 54.4256
0.85417 | 18446 | 381.19 | 54.4256
0.86458 | 18446 | 381.19 | 54.4256
0.875 | 18446 | 381.19 | 54.4256
0.88542 | 18446 | 381.19 | 54.4256
0.89583 | 18446 | 381.19 | 54.4256
0.90625 | 18446 | 381.19 | 54.4256
0.91667 | 18446 | 381.19 | 54.4256
0.92708 | 18446 | 381.19 | 54.4256
0.9375 | 18446 | 381.19 | 54.4256
0.94792 | 18446 | 381.19 | 54.4256
0.95833 | 18446 | 381.19 | 54.4256
0.96875 | 18446 | 381.19 | 54.4256
0.97917 | 18446 | 381.19 | 54.4256
0.98958 | 18446 | 381.19 | 54.4256
1 | 18446 | 381.19 | 54.4256
1.0104 | 21474 | 405.876 | 54.2133
1.0208 | 19620 | 399.989 | 54.459
1.0312 | 19334 | 394.865 | 54.7792
1.0417 | 18978 | 391.764 | 56.1501
1.0521 | 18321 | 388.441 | 57.984
1.0625 | 17855 | 398.902 | 61.4396
1.0729 | 17237 | 388.491 | 60.8017
1.0833 | 16453 | 375.328 | 58.8446
1.0938 | 16548 | 365.261 | 57.828
1.1042 | 16295 | 353.352 | 54.8502
1.1146 | 14743 | 341.929 | 54.3289
1.125 | 14743 | 341.929 | 54.3289
1.1354 | 13613 | 320.789 | 50.0572
1.1458 | 12807 | 308.975 | 47.2126
1.1562 | 12173 | 292.417 | 43.2385
1.1667 | 11533 | 276.711 | 39.8134
1.1771 | 12198 | 266.791 | 37.9419
1.1875 | 11640 | 256.39 | 36.0749
1.1979 | 11978 | 247.469 | 33.6307
1.2083 | 13272 | 246.049 | 33.9029
1.2188 | 12452 | 242.006 | 33.817
1.2292 | 13453 | 240.775 | 33.8495
1.2396 | 13815 | 241.083 | 33.8232
1.25 | 13803 | 240.417 | 33.7176
1.2604 | 12542 | 233.436 | 33.0814
1.2708 | 11865 | 228.794 | 32.7439
1.2812 | 12118 | 225.718 | 32.3479
1.2917 | 11906 | 222.562 | 32.032
1.3021 | 12059 | 220.665 | 31.9285
1.3125 | 12446 | 220.054 | 32.0348
1.3229 | 12982 | 220.996 | 32.4383
1.3333 | 12956 | 221.556 | 32.8965
1.3438 | 12745 | 221.863 | 33.279
1.3542 | 13597 | 224.497 | 33.9482
1.3646 | 14171 | 229.249 | 34.8338
1.375 | 14171 | 229.249 | 34.8338
1.3854 | 17637 | 242.485 | 38.5688
1.3958 | 17635 | 264.33 | 45.2445
1.4062 | 22461 | 298.601 | 52.6706
1.4167 | 26276 | 337.077 | 59.3141
1.4271 | 25598 | 375.399 | 67.5693
1.4375 | 27780 | 413.696 | 73.7548
1.4479 | 29551 | 452.36 | 79.3185
1.4583 | 31861 | 486.992 | 82.7013
1.4688 | 32171 | 512.038 | 83.4993
1.4792 | 32180 | 527.073 | 80.6565
1.4896 | 31869 | 534.619 | 75.81
1.5 | 28047 | 530.642 | 72.7503
1.5104 | 26690 | 514.116 | 66.1859
1.5208 | 25572 | 503.532 | 63.0469
1.5312 | 25496 | 496.76 | 61.0328
1.5417 | 22401 | 482.346 | 58.5822
1.5521 | 26555 | 487.172 | 58.9774
1.5625 | 25905 | 488.184 | 58.195
1.5729 | 24310 | 483.723 | 57.1044
1.5833 | 23404 | 478.181 | 56.8374
1.5938 | 20560 | 463.806 | 54.995
1.6042 | 18732 | 443.922 | 53.4856
1.6146 | 25320 | 451.218 | 53.7971
1.625 | 25320 | 451.218 | 53.7971
1.6354 | 23046 | 445.711 | 52.6887
1.6458 | 21357 | 436.331 | 51.9174
1.6562 | 22487 | 433.833 | 52.4168
1.6667 | 18221 | 417.816 | 51.3897
1.6771 | 17442 | 402.053 | 50.2781
1.6875 | 19246 | 397.534 | 50.6766
1.6979 | 19197 | 394.731 | 51.5771
1.7083 | 19637 | 392.367 | 51.4381
1.7188 | 19014 | 386.358 | 50.3783
1.7292 | 18480 | 376.467 | 48.5387
1.7396 | 18208 | 368.187 | 47.8773
1.75 | 18547 | 364.455 | 47.7202
1.7604 | 18670 | 363.481 | 49.5326
1.7708 | 18654 | 364.512 | 50.6437
1.7812 | 23137 | 376.541 | 53.2088
1.7917 | 22509 | 383.808 | 53.4958
1.8021 | 22031 | 388.158 | 51.2442
1.8125 | 22489 | 398.101 | 53.6977
1.8229 | 18876 | 391.676 | 52.9122
1.8333 | 20674 | 394.139 | 53.8248
1.8438 | 24145 | 409.78 | 57.1672
1.8542 | 22518 | 417.213 | 59.166
1.8646 | 22803 | 423.276 | 60.1623
1.875 | 22803 | 423.276 | 60.1623
1.8854 | 21780 | 426.09 | 61.6272
1.8958 | 19067 | 420.05 | 61.441
1.9062 | 26211 | 439.142 | 63.4727
1.9167 | 24096 | 445.193 | 63.0497
1.9271 | 23071 | 445.77 | 63.1375
1.9375 | 22388 | 443.7 | 62.7881
1.9479 | 17483 | 424.981 | 60.6968
1.9583 | 25814 | 438.815 | 62.1559
1.9688 | 23248 | 438.995 | 60.8938
1.9792 | 24098 | 440.224 | 59.4942
1.9896 | 22402 | 435.94 | 57.6494
2 | 19962 | 424.663 | 55.7783
2.0104 | 18618 | 398.5 | 53.4007
2.0208 | 19046 | 393.304 | 54.0075
2.0312 | 23433 | 403.839 | 55.8545
2.0417 | 22011 | 408.218 | 57.4939
2.0521 | 23310 | 417.413 | 60.3045
2.0625 | 23158 | 425.681 | 63.6883
2.0729 | 15122 | 402.222 | 61.2693
2.0833 | 15319 | 383.34 | 59.1363
2.0938 | 15342 | 368.602 | 57.8635
2.1042 | 14751 | 351.82 | 54.5865
2.1146 | 14287 | 339.78 | 54.1525
2.125 | 14287 | 339.78 | 54.1525
2.1354 | 12478 | 319.354 | 49.8604
2.1458 | 12477 | 306.971 | 47.074
2.1562 | 11347 | 288.387 | 42.9496
2.1667 | 11037 | 272.158 | 39.5317
2.1771 | 10473 | 258.031 | 37.3391
2.1875 | 10000 | 244.708 | 35.3368
2.1979 | 11258 | 236.118 | 32.9808
2.2083 | 10436 | 228.58 | 32.7737
2.2188 | 10976 | 223.715 | 32.7521
2.2292 | 11250 | 219.452 | 32.5682
2.2396 | 11740 | 217.583 | 32.4339
2.25 | 11562 | 214.543 | 32.1927
2.2604 | 12578 | 214.146 | 32.0666
2.2708 | 11399 | 210.837 | 31.773
2.2812 | 11448 | 208.333 | 31.3923
2.2917 | 12090 | 208.104 | 31.2846
2.3021 | 12429 | 209.075 | 31.3436
2.3125 | 11500 | 207.25 | 31.3023
2.3229 | 11717 | 206.549 | 31.5964
2.3333 | 11751 | 206.058 | 32.0027
2.3438 | 11489 | 205.392 | 32.3337
2.3542 | 12859 | 208.553 | 33.0549
2.3646 | 12350 | 210.671 | 33.7288
2.375 | 12350 | 210.671 | 33.7288
2.3854 | 12194 | 215.612 | 36.7541
2.3958 | 15329 | 235.446 | 43.5038
2.4062 | 22901 | 274.793 | 51.343
2.4167 | 23690 | 308.419 | 57.3951
2.4271 | 24749 | 348.238 | 65.8921
2.4375 | 27249 | 388.599 | 72.1992
2.4479 | 29504 | 430.668 | 78.0019
2.4583 | 31868 | 471.119 | 81.728
2.4688 | 32126 | 501.093 | 82.8186
2.4792 | 31909 | 519.703 | 80.1566
2.4896 | 31927 | 531.491 | 75.6279
2.5 | 31719 | 540.931 | 74.0525
2.5104 | 27039 | 534.318 | 67.4458
2.5208 | 25844 | 522.549 | 64.2126
2.5312 | 25174 | 510.637 | 61.7853
2.5417 | 24783 | 502.414 | 60.1624
2.5521 | 24444 | 495.288 | 59.0782
2.5625 | 22762 | 484.346 | 57.4217
2.5729 | 24940 | 484.59 | 57.265
2.5833 | 24113 | 481.797 | 57.1684
2.5938 | 23320 | 476.538 | 56.182
2.6042 | 22247 | 467.756 | 55.3934
2.6146 | 21875 | 456.89 | 53.5688
2.625 | 21875 | 456.89 | 53.5688
2.6354 | 21863 | 447.211 | 52.5853
2.6458 | 21236 | 438.046 | 51.995
2.6562 | 21473 | 432.225 | 52.1678
2.6667 | 20822 | 426.133 | 52.244
2.6771 | 20463 | 420.443 | 51.7382
2.6875 | 20034 | 415.884 | 51.8146
2.6979 | 19328 | 411.428 | 52.5267
2.7083 | 18928 | 403.512 | 51.9631
2.7188 | 18510 | 394.292 | 50.7516
2.7292 | 18319 | 383.021 | 48.8803
2.7396 | 18224 | 375.88 | 48.3045
2.75 | 19106 | 372.828 | 48.2564
2.7604 | 21604 | 388.29 | 51.3019
2.7708 | 22228 | 395.84 | 52.869
2.7812 | 21169 | 395.293 | 54.0189
2.7917 | 19849 | 391.428 | 53.5743
2.8021 | 17451 | 380.798 | 50.2302
2.8125 | 18335 | 380.482 | 52.158
2.8229 | 22018 | 389.449 | 53.2013
2.8333 | 23369 | 400.713 | 54.563
2.8438 | 23270 | 411.344 | 57.1361
2.8542 | 25050 | 426.904 | 60.0863
2.8646 | 21540 | 426.313 | 60.1561
2.875 | 21540 | 426.313 | 60.1561
2.8854 | 19321 | 420.609 | 60.9717
2.8958 | 21190 | 423.674 | 61.9397
2.9062 | 26591 | 443.175 | 63.7658
2.9167 | 24225 | 448.869 | 63.2819
2.9271 | 23902 | 451.657 | 63.6021
2.9375 | 24339 | 455.04 | 63.7372
2.9479 | 21529 | 447.472 | 62.5475
2.9583 | 26978 | 460.136 | 63.5916
2.9688 | 25693 | 464.394 | 62.7504
2.9792 | 24779 | 462.814 | 60.9135
2.9896 | 24086 | 460.173 | 59.3084
3 | 23308 | 455.71 | 58.0596
3.0104 | 21014 | 433.315 | 55.7004
3.0208 | 19118 | 405.874 | 54.7168
3.0312 | 18847 | 406.265 | 55.3458
3.0417 | 18509 | 402.748 | 56.6962
3.0521 | 17886 | 400.461 | 58.5891
3.0625 | 17445 | 399.241 | 61.4037
3.0729 | 16858 | 392.979 | 60.9977
3.0833 | 16116 | 396.435 | 59.9493
3.0938 | 16206 | 383.436 | 58.775
3.1042 | 15965 | 368.325 | 55.6244
3.1146 | 14494 | 359.929 | 55.2555
3.125 | 14494 | 359.929 | 55.2555
3.1354 | 13423 | 344.187 | 51.2796
3.1458 | 12660 | 333.85 | 48.5108
3.1562 | 12059 | 317.058 | 44.5214
3.1667 | 11453 | 300.831 | 41.0666
3.1771 | 12083 | 286.664 | 38.9758
3.1875 | 11554 | 272.898 | 36.9315
3.1979 | 11875 | 262.401 | 34.405
3.2083 | 13101 | 254.173 | 34.3194
3.2188 | 12323 | 248.221 | 34.1346
3.2292 | 13271 | 246.103 | 34.118
3.2396 | 13614 | 242.043 | 33.8589
3.25 | 13604 | 240.755 | 33.7206
3.2604 | 12408 | 240.457 | 33.4415
3.2708 | 11767 | 236.243 | 33.1271
3.2812 | 12006 | 233.013 | 32.7229
3.2917 | 11805 | 228.517 | 32.3364
3.3021 | 11951 | 225.931 | 32.1976
3.3125 | 12317 | 223.087 | 32.1857
3.3229 | 12825 | 221.208 | 32.4389
3.3333 | 12800 | 220.628 | 32.8368
3.3438 | 12600 | 221.957 | 33.2747
3.3542 | 13408 | 222.805 | 33.845
3.3646 | 13952 | 223.935 | 34.5356
3.375 | 13952 | 223.935 | 34.5356
3.3854 | 17235 | 230.837 | 37.9001
3.3958 | 17233 | 245.177 | 44.1624
3.4062 | 21804 | 265.157 | 50.7095
3.4167 | 25418 | 284.426 | 56.145
3.4271 | 24776 | 322.005 | 64.367
3.4375 | 26842 | 362.795 | 70.6261
3.4479 | 28519 | 395.642 | 75.7771
3.4583 | 30707 | 427.852 | 78.9243
3.4688 | 31000 | 456.023 | 79.8884
3.4792 | 31009 | 478.98 | 77.5175
3.4896 | 30713 | 495.397 | 73.2112
3.5 | 27093 | 509.635 | 71.3304
3.5104 | 25808 | 516.967 | 66.1931
3.5208 | 24748 | 510.469 | 63.3037
3.5312 | 24677 | 503.054 | 61.2522
3.5417 | 21745 | 495.89 | 59.239
3.5521 | 25678 | 493.274 | 59.1811
3.5625 | 25062 | 480.696 | 57.6101
3.5729 | 23552 | 487.077 | 57.1669
3.5833 | 22693 | 489.366 | 57.3575
3.5938 | 20001 | 485.226 | 56.1043
3.6042 | 18269 | 478.271 | 55.3134
3.6146 | 24508 | 460.124 | 54.1847
3.625 | 24508 | 460.124 | 54.1847
3.6354 | 22354 | 437.134 | 52.0876
3.6458 | 20755 | 445.688 | 52.3517
3.6562 | 21824 | 442.89 | 52.8289
3.6667 | 17785 | 435.839 | 52.3177
3.6771 | 17047 | 434.983 | 52.0261
3.6875 | 18755 | 420.746 | 51.8986
3.6979 | 18708 | 407.608 | 52.2271
3.7083 | 19125 | 400.63 | 51.8303
3.7188 | 18535 | 392.776 | 50.6708
3.7292 | 18029 | 386.203 | 49.018
3.7396 | 17772 | 380.609 | 48.5057
3.75 | 18093 | 374.177 | 48.2
3.7604 | 18209 | 367.506 | 49.6982
3.7708 | 18193 | 368.129 | 50.7874
3.7812 | 22437 | 365.306 | 52.4771
3.7917 | 21842 | 363.401 | 52.2469
3.8021 | 21390 | 376.101 | 50.4752
3.8125 | 21824 | 387.915 | 53.0275
3.8229 | 18403 | 393.24 | 52.9362
3.8333 | 20104 | 400.066 | 54.082
3.8438 | 23390 | 396.287 | 56.2854
3.8542 | 21850 | 401.222 | 58.1622
3.8646 | 22120 | 415.236 | 59.6067
3.875 | 22120 | 415.236 | 59.6067
3.8854 | 21151 | 421.553 | 61.2805
3.8958 | 18582 | 428.336 | 61.8339
3.9062 | 25345 | 429.74 | 62.7953
3.9167 | 23343 | 421.569 | 61.576
3.9271 | 22372 | 438.576 | 62.6222
3.9375 | 21725 | 442.859 | 62.641
3.9479 | 17083 | 442.424 | 61.5958
3.9583 | 24968 | 439.346 | 62.0609
3.9688 | 22540 | 420.363 | 59.7205
3.9792 | 23343 | 432.824 | 58.9533
3.9896 | 21738 | 432.716 | 57.3657
4 | 19429 | 435.736 | 56.3188
4.0104 | 18156 | 418.73 | 54.4544
4.0208 | 18561 | 406.677 | 54.6824
4.0312 | 22713 | 398.89 | 55.4699
4.0417 | 21366 | 396.066 | 56.7138
4.0521 | 22596 | 409.429 | 59.7438
4.0625 | 22452 | 415.684 | 63.0135
4.0729 | 14847 | 421.931 | 62.2922
4.0833 | 15033 | 423.196 | 61.2461
4.0938 | 15055 | 397.158 | 59.3662
4.1042 | 14496 | 376.33 | 55.8715
4.1146 | 14056 | 363.267 | 55.3816
4.125 | 14056 | 363.267 | 55.3816
4.1354 | 12345 | 342.654 | 51.0731
4.1458 | 12344 | 331.926 | 48.3744
4.1562 | 11274 | 315.622 | 44.3627
4.1667 | 10981 | 298.828 | 40.915
4.1771 | 10448 | 282.636 | 38.6115
4.1875 | 10000 | 268.347 | 36.5567
4.1979 | 11190 | 253.645 | 33.8895
4.2083 | 10412 | 242.497 | 33.4925
4.2188 | 10923 | 236.877 | 33.4322
4.2292 | 11182 | 228.643 | 33.0422
4.2396 | 11646 | 223.762 | 32.7508
4.25 | 11478 | 219.443 | 32.4442
4.2604 | 12439 | 214.596 | 32.0814
4.2708 | 11323 | 213.56 | 31.91
4.2812 | 11370 | 213.733 | 31.6694
4.2917 | 11977 | 210.569 | 31.4074
4.3021 | 12298 | 208.554 | 31.3076
4.3125 | 11419 | 208.637 | 31.3696
4.3229 | 11624 | 209.623 | 31.751
4.3333 | 11656 | 207.83 | 32.0901
4.3438 | 11409 | 207.518 | 32.4399
4.3542 | 12704 | 207.316 | 32.9796
4.3646 | 12223 | 207.473 | 33.553
4.375 | 12223 | 207.473 | 33.553
4.3854 | 12076 | 214.902 | 36.7102
4.3958 | 15040 | 226.609 | 43.0091
4.4062 | 22202 | 238.297 | 49.2052
4.4167 | 22948 | 255.559 | 54.2938
4.4271 | 23950 | 298.211 | 62.9163
4.4375 | 26314 | 334.153 | 68.8839
4.4479 | 28447 | 368.497 | 74.1426
4.4583 | 30682 | 402.767 | 77.3936
4.4688 | 30926 | 434.341 | 78.5554
4.4792 | 30720 | 463.112 | 76.5077
4.4896 | 30737 | 484.454 | 72.5487
4.5 | 30540 | 502.265 | 71.479
4.5104 | 26113 | 527.245 | 66.8543
4.5208 | 24983 | 533.06 | 64.6641
4.5312 | 24349 | 523.24 | 62.3649
4.5417 | 23979 | 514.893 | 60.7385
4.5521 | 23658 | 507.141 | 59.6223
4.5625 | 22068 | 500.749 | 58.2353
4.5729 | 24127 | 495.185 | 57.7369
4.5833 | 23345 | 485.528 | 57.2504
4.5938 | 22595 | 486.089 | 56.6056
4.6042 | 21580 | 481.879 | 56.0848
4.6146 | 21228 | 472.845 | 54.3665
4.625 | 21228 | 472.845 | 54.3665
4.6354 | 21217 | 460.952 | 53.2605
4.6458 | 20623 | 451.353 | 52.65
4.6562 | 20848 | 444.386 | 52.7577
4.6667 | 20232 | 437.551 | 52.796
4.6771 | 19893 | 433.371 | 52.3779
4.6875 | 19487 | 429.056 | 52.4705
4.6979 | 18819 | 425.985 | 53.2629
4.7083 | 18441 | 418.967 | 52.7517
4.7188 | 18045 | 409.461 | 51.5261
4.7292 | 17864 | 397.339 | 49.6093
4.7396 | 17775 | 388.533 | 48.9427
4.75 | 18608 | 380.723 | 48.6296
4.7604 | 20969 | 375.871 | 50.5147
4.7708 | 21559 | 387.657 | 52.3128
4.7812 | 20558 | 390.1 | 53.6433
4.7917 | 19310 | 394.71 | 53.6845
4.8021 | 17043 | 394.839 | 50.9452
4.8125 | 17878 | 395.529 | 52.9297
4.8229 | 21360 | 385.882 | 52.9125
4.8333 | 22636 | 382.453 | 53.4169
4.8438 | 22542 | 394.058 | 56.0453
4.8542 | 24225 | 407.791 | 58.8591
4.8646 | 20907 | 416.799 | 59.5274
4.875 | 20907 | 416.799 | 59.5274
4.8854 | 18809 | 431.235 | 61.4901
4.8958 | 20576 | 431.369 | 62.2881
4.9062 | 25680 | 424.259 | 62.5216
4.9167 | 23444 | 425.189 | 61.7995
4.9271 | 23139 | 442.605 | 62.9656
4.9375 | 23551 | 446.529 | 63.1246
4.9479 | 20895 | 448.304 | 62.498
4.9583 | 26044 | 450.677 | 62.8879
4.9688 | 24830 | 442.837 | 61.3545
4.9792 | 23966 | 454.13 | 60.2793
4.9896 | 23311 | 458.097 | 59.0631
5 | 22576 | 458.31 | 58.0896
5.0104 | 20408 | 449.755 | 56.5323
5.0208 | 18616 | 399.989 | 54.3197
5.0312 | 18359 | 394.865 | 54.6464
5.0417 | 18040 | 391.764 | 56.0247
5.0521 | 17452 | 388.442 | 57.8703
5.0625 | 17034 | 398.901 | 61.3299
5.0729 | 16480 | 388.491 | 60.7043
5.0833 | 15778 | 375.328 | 58.7609
5.0938 | 15863 | 365.261 | 57.7455
5.1042 | 15636 | 353.352 | 54.773
5.1146 | 14246 | 341.704 | 54.2506
5.125 | 14246 | 341.704 | 54.2506
5.1354 | 13234 | 320.789 | 50.0168
5.1458 | 12513 | 308.975 | 47.1829
5.1562 | 11946 | 292.417 | 43.2167
5.1667 | 11373 | 276.711 | 39.7989
5.1771 | 11968 | 266.792 | 37.922
5.1875 | 11468 | 256.391 | 36.0607
5.1979 | 11771 | 247.469 | 33.6141
5.2083 | 12929 | 246.049 | 33.8758
5.2188 | 12195 | 242.005 | 33.7971
5.2292 | 13090 | 240.775 | 33.8217
5.2396 | 13414 | 241.083 | 33.7925
5.25 | 13404 | 240.418 | 33.687
5.2604 | 12275 | 233.437 | 33.0618
5.2708 | 11669 | 228.794 | 32.7299
5.2812 | 11895 | 225.718 | 32.3323
5.2917 | 11705 | 222.563 | 32.0183
5.3021 | 11843 | 220.665 | 31.9139
5.3125 | 12189 | 220.054 | 32.0175
5.3229 | 12669 | 220.996 | 32.417
5.3333 | 12645 | 221.556 | 32.8755
5.3438 | 12456 | 221.863 | 33.2595
5.3542 | 13219 | 224.498 | 33.9222
5.3646 | 13732 | 229.249 | 34.8031
5.375 | 13732 | 229.249 | 34.8031
5.3854 | 16832 | 242.485 | 38.5095
5.3958 | 16830 | 264.33 | 45.1813
5.4062 | 21148 | 298.6 | 52.554
5.4167 | 24560 | 337.077 | 59.1388
5.4271 | 23953 | 375.399 | 67.3838
5.4375 | 25904 | 413.696 | 73.5202
5.4479 | 27488 | 452.36 | 79.0333
5.4583 | 29553 | 486.992 | 82.3513
5.4688 | 29829 | 512.038 | 83.1167
5.4792 | 29837 | 527.074 | 80.2506
5.4896 | 29558 | 534.619 | 75.3918
5.5 | 26139 | 530.642 | 72.4019
5.5104 | 24925 | 514.117 | 65.8659
5.5208 | 23924 | 503.532 | 62.7521
5.5312 | 23857 | 496.759 | 60.7403
5.5417 | 21088 | 482.346 | 58.3554
5.5521 | 24802 | 487.172 | 58.6697
5.5625 | 24220 | 488.185 | 57.8984
5.5729 | 22794 | 483.723 | 56.8406
5.5833 | 21983 | 478.182 | 56.5945
5.5938 | 19441 | 463.805 | 54.8111
5.6042 | 17806 | 443.922 | 53.3417
5.6146 | 23695 | 451.218 | 53.5368
5.625 | 23695 | 451.218 | 53.5368
5.6354 | 21662 | 445.711 | 52.4682
5.6458 | 20152 | 436.331 | 51.7294
5.6562 | 21161 | 433.833 | 52.2112
5.6667 | 17348 | 417.816 | 51.2607
5.6771 | 16651 | 402.052 | 50.1672
5.6875 | 18264 | 397.534 | 50.5418
5.6979 | 18220 | 394.731 | 51.4456
5.7083 | 18613 | 392.367 | 51.3013
5.7188 | 18056 | 386.359 | 50.2523
5.7292 | 17578 | 376.468 | 48.4223
5.7396 | 17335 | 368.187 | 47.7673
5.75 | 17638 | 364.455 | 47.6068
5.7604 | 17747 | 363.481 | 49.4192
5.7708 | 17733 | 364.512 | 50.5312
5.7812 | 21738 | 376.541 | 53.0298
5.7917 | 21176 | 383.808 | 53.3209
5.8021 | 20749 | 388.158 | 51.0733
5.8125 | 21158 | 398.101 | 53.517
5.8229 | 17930 | 391.676 | 52.7868
5.8333 | 19535 | 394.139 | 53.6733
5.8438 | 22636 | 409.78 | 56.9581
5.8542 | 21182 | 417.213 | 58.9787
5.8646 | 21436 | 423.276 | 59.968
5.875 | 21436 | 423.276 | 59.968
5.8854 | 20522 | 426.09 | 61.4483
5.8958 | 18098 | 420.05 | 61.307
5.9062 | 24479 | 439.141 | 63.2192
5.9167 | 22590 | 445.192 | 62.8253
5.9271 | 21673 | 445.769 | 62.9284
5.9375 | 21063 | 443.699 | 62.5903
5.9479 | 16683 | 424.981 | 60.5834
5.9583 | 24122 | 438.815 | 61.9038
5.9688 | 21831 | 438.995 | 60.6811
5.9792 | 22589 | 440.223 | 59.2644
5.9896 | 21074 | 435.94 | 57.4484
6 | 18895 | 424.663 | 55.6212
6.0104 | 16990 | 331.66 | 49.5169
6.0208 | 15964 | 328.748 | 50.0852
6.0312 | 15806 | 334.966 | 51.0516
6.0417 | 15610 | 338.529 | 52.819
6.0521 | 15247 | 345.206 | 55.2486
6.0625 | 14989 | 351.794 | 58.5205
6.0729 | 14647 | 338.589 | 57.7894
6.0833 | 14212 | 326.681 | 55.9646
6.0938 | 14266 | 317.322 | 54.9879
6.1042 | 14126 | 305.764 | 52.0524
6.1146 | 13264 | 298.654 | 51.8564
6.125 | 13264 | 298.654 | 51.8564
6.1354 | 12636 | 283.361 | 47.9766
6.1458 | 12189 | 276.608 | 45.4481
6.1562 | 11836 | 264.125 | 41.7228
6.1667 | 11481 | 253.269 | 38.5838
6.1771 | 11851 | 244.348 | 36.736
6.1875 | 11540 | 235.974 | 34.9997
6.1979 | 11729 | 229.963 | 32.694
6.2083 | 12450 | 225.821 | 32.7715
6.2188 | 11994 | 223.206 | 32.7946
6.2292 | 12552 | 220.635 | 32.7174
6.2396 | 12755 | 219.725 | 32.6135
6.25 | 12749 | 217.828 | 32.4437
6.2604 | 12046 | 217.63 | 32.2152
6.2708 | 11668 | 215.643 | 32.0419
6.2812 | 11810 | 214.125 | 31.7186
6.2917 | 11692 | 213.966 | 31.5665
6.3021 | 11778 | 214.649 | 31.5945
6.3125 | 11994 | 213.705 | 31.6718
6.3229 | 12294 | 213.435 | 31.9941
6.3333 | 12280 | 213.269 | 32.4142
6.3438 | 12162 | 213.185 | 32.7838
6.3542 | 12640 | 215.238 | 33.394
6.3646 | 12962 | 217.104 | 34.1071
6.375 | 12962 | 217.104 | 34.1071
6.3854 | 14903 | 221.997 | 37.2643
6.3958 | 14903 | 238.126 | 43.6203
6.4062 | 17608 | 265.681 | 50.4294
6.4167 | 19748 | 288.665 | 55.9379
6.4271 | 19370 | 317.918 | 63.6591
6.4375 | 20596 | 345.785 | 69.0288
6.4479 | 21592 | 374.034 | 73.7682
6.4583 | 22891 | 399.399 | 76.3136
6.4688 | 23068 | 416.261 | 76.5079
6.4792 | 23077 | 424.12 | 73.1623
6.4896 | 22905 | 426.867 | 68.0025
6.5 | 20762 | 429.12 | 65.6899
6.5104 | 20005 | 419.678 | 59.6768
6.5208 | 19379 | 410.599 | 56.7522
6.5312 | 19339 | 401.486 | 54.6182
6.5417 | 17601 | 395.896 | 52.9966
6.5521 | 19939 | 391.3 | 52.4411
6.5625 | 19576 | 384.906 | 51.3064
6.5729 | 18681 | 385.221 | 50.6582
6.5833 | 18173 | 384.074 | 50.7412
6.5938 | 16574 | 381.34 | 49.8416
6.6042 | 15545 | 376.127 | 49.3228
6.6146 | 19259 | 368.552 | 48.2172
6.625 | 19259 | 368.552 | 48.2172
6.6354 | 17980 | 361.503 | 47.2342
6.6458 | 17030 | 355.44 | 46.8131
6.6562 | 17669 | 351.76 | 47.1508
6.6667 | 15264 | 348.452 | 47.2093
6.6771 | 14826 | 345.533 | 46.873
6.6875 | 15846 | 343.854 | 47.299
6.6979 | 15819 | 342.747 | 48.3049
6.7083 | 16069 | 338.081 | 48.0123
6.7188 | 15719 | 332.083 | 47.0043
6.7292 | 15418 | 323.696 | 45.2919
6.7396 | 15266 | 319.073 | 44.8557
6.75 | 15459 | 316.907 | 44.7646
6.7604 | 15531 | 327.252 | 47.1876
6.7708 | 15524 | 332.832 | 48.5483
6.7812 | 18062 | 332.175 | 50.1097
6.7917 | 17708 | 329.891 | 49.8971
6.8021 | 17440 | 323.65 | 47.0883
6.8125 | 17701 | 325.33 | 49.0408
6.8229 | 15656 | 330.898 | 49.1948
6.8333 | 16676 | 338.019 | 50.2296
6.8438 | 18646 | 345.666 | 52.8482
6.8542 | 17726 | 356.327 | 55.141
6.8646 | 17889 | 356.764 | 55.7966
6.875 | 17889 | 356.764 | 55.7966
6.8854 | 17311 | 354.572 | 57.066
6.8958 | 15773 | 357.441 | 57.5921
6.9062 | 19830 | 369.355 | 58.6288
6.9167 | 18631 | 372.87 | 58.2234
6.9271 | 18051 | 374.18 | 58.434
6.9375 | 17665 | 375.615 | 58.3352
6.9479 | 14880 | 370.46 | 57.3949
6.9583 | 19617 | 376.895 | 57.7698
6.9688 | 18161 | 378.534 | 56.7891
6.9792 | 18646 | 376.09 | 55.1058
6.9896 | 17683 | 373.579 | 53.5013
7 | 16297 | 370.197 | 52.2749
7.0104 | 15534 | 354.752 | 50.6085
7.0208 | 15779 | 328.749 | 50.0655
7.0312 | 18281 | 334.966 | 51.322
7.0417 | 17472 | 338.529 | 53.0234
7.0521 | 18215 | 345.206 | 55.579
7.0625 | 18130 | 351.794 | 58.8735
7.0729 | 13548 | 338.589 | 57.6727
7.0833 | 13661 | 326.681 | 55.9083
7.0938 | 13676 | 317.322 | 54.9294
7.1042 | 13339 | 305.764 | 51.977
7.1146 | 13075 | 298.653 | 51.8388
7.125 | 13075 | 298.653 | 51.8388
7.1354 | 12042 | 283.361 | 47.9233
7.1458 | 12042 | 276.608 | 45.4355
7.1562 | 11397 | 264.124 | 41.6864
7.1667 | 11220 | 253.269 | 38.563
7.1771 | 10898 | 244.347 | 36.663
7.1875 | 10627 | 235.973 | 34.9325
7.1979 | 11347 | 229.963 | 32.6665
7.2083 | 10876 | 225.821 | 32.6614
7.2188 | 11186 | 223.206 | 32.7391
7.2292 | 11343 | 220.635 | 32.6356
7.2396 | 11624 | 219.725 | 32.5377
7.25 | 11522 | 217.828 | 32.3623
7.2604 | 12105 | 217.63 | 32.2191
7.2708 | 11429 | 215.643 | 32.0262
7.2812 | 11457 | 214.125 | 31.6958
7.2917 | 11826 | 213.966 | 31.5752
7.3021 | 12021 | 214.649 | 31.6103
7.3125 | 11488 | 213.704 | 31.6392
7.3229 | 11613 | 213.435 | 31.9504
7.3333 | 11632 | 213.269 | 32.3728
7.3438 | 11482 | 213.184 | 32.7405
7.3542 | 12270 | 215.239 | 33.3703
7.3646 | 11978 | 217.105 | 34.0437
7.375 | 11978 | 217.105 | 34.0437
7.3854 | 11889 | 221.997 | 37.07
7.3958 | 13692 | 238.127 | 43.5396
7.4062 | 18050 | 265.682 | 50.4621
7.4167 | 18506 | 288.665 | 55.8381
7.4271 | 19118 | 317.918 | 63.6372
7.4375 | 20560 | 345.785 | 69.0254
7.4479 | 21862 | 374.034 | 73.796
7.4583 | 23227 | 399.399 | 76.3514
7.4688 | 23379 | 416.261 | 76.5453
7.4792 | 23258 | 424.12 | 73.1852
7.4896 | 23272 | 426.868 | 68.0511
7.5 | 23155 | 429.121 | 66.0177
7.5104 | 20461 | 419.677 | 59.74
7.5208 | 19774 | 410.6 | 56.8065
7.5312 | 19390 | 401.486 | 54.6251
7.5417 | 19166 | 395.896 | 53.2063
7.5521 | 18973 | 391.3 | 52.3131
7.5625 | 18003 | 384.906 | 51.1024
7.5729 | 19264 | 385.221 | 50.7339
7.5833 | 18789 | 384.074 | 50.8204
7.5938 | 18332 | 381.34 | 50.0653
7.6042 | 17713 | 376.127 | 49.5938
7.6146 | 17500 | 368.552 | 48.0008
7.625 | 17500 | 368.552 | 48.0008
7.6354 | 17495 | 361.503 | 47.1754
7.6458 | 17134 | 355.44 | 46.8255
7.6562 | 17273 | 351.76 | 47.1041
7.6667 | 16898 | 348.452 | 47.3997
7.6771 | 16692 | 345.533 | 47.0874
7.6875 | 16445 | 343.854 | 47.3668
7.6979 | 16037 | 342.747 | 48.3291
7.7083 | 15806 | 338.081 | 47.9836
7.7188 | 15565 | 332.082 | 46.9879
7.7292 | 15456 | 323.697 | 45.2959
7.7396 | 15402 | 319.073 | 44.8699
7.75 | 15915 | 316.907 | 44.8118
7.7604 | 17370 | 327.252 | 47.3835
7.7708 | 17735 | 332.832 | 48.7867
7.7812 | 17121 | 332.174 | 50.0082
7.7917 | 16355 | 329.89 | 49.7523
7.8021 | 14962 | 323.651 | 46.8301
7.8125 | 15477 | 325.331 | 48.8117
7.8229 | 17623 | 330.898 | 49.4017
7.8333 | 18411 | 338.02 | 50.4167
7.8438 | 18356 | 345.666 | 52.8164
7.8542 | 19395 | 356.327 | 55.3293
7.8646 | 17352 | 356.764 | 55.7363
7.875 | 17352 | 356.764 | 55.7363
7.8854 | 16060 | 354.572 | 56.9284
7.8958 | 17152 | 357.44 | 57.744
7.9062 | 20304 | 369.356 | 58.6834
7.9167 | 18926 | 372.87 | 58.2577
7.9271 | 18740 | 374.18 | 58.5149
7.9375 | 18997 | 375.615 | 58.4932
7.9479 | 17359 | 370.46 | 57.6853
7.9583 | 20544 | 376.896 | 57.8821
7.9688 | 19796 | 378.534 | 56.9899
7.9792 | 19265 | 376.091 | 55.1821
7.9896 | 18862 | 373.58 | 53.6467
8 | 18409 | 370.196 | 52.5341
8.0104 | 21474 | 405.876 | 54.2133
8.0208 | 19620 | 399.989 | 54.459
8.0312 | 19334 | 394.865 | 54.7792
8.0417 | 18978 | 391.764 | 56.1501
8.0521 | 18321 | 388.441 | 57.984
8.0625 | 17855 | 398.902 | 61.4396
8.0729 | 17237 | 388.491 | 60.8017
8.0833 | 16453 | 375.328 | 58.8446
8.0938 | 16548 | 365.261 | 57.828
8.1042 | 16295 | 353.352 | 54.8502
8.1146 | 14743 | 341.929 | 54.3289
8.125 | 14743 | 341.929 | 54.3289
8.1354 | 13613 | 320.789 | 50.0572
8.1458 | 12807 | 308.975 | 47.2126
8.1562 | 12173 | 292.417 | 43.2385
8.1667 | 11533 | 276.711 | 39.8134
8.1771 | 12198 | 266.791 | 37.9419
8.1875 | 11640 | 256.39 | 36.0749
8.1979 | 11978 | 247.469 | 33.6307
8.2083 | 13272 | 246.049 | 33.9029
8.2188 | 12452 | 242.006 | 33.817
8.2292 | 13453 | 240.775 | 33.8495
8.2396 | 13815 | 241.083 | 33.8232
8.25 | 13803 | 240.417 | 33.7176
8.2604 | 12542 | 233.436 | 33.0814
8.2708 | 11865 | 228.794 | 32.7439
8.2812 | 12118 | 225.718 | 32.3479
8.2917 | 11906 | 222.562 | 32.032
8.3021 | 12059 | 220.665 | 31.9285
8.3125 | 12446 | 220.054 | 32.0348
8.3229 | 12982 | 220.996 | 32.4383
8.3333 | 12956 | 221.556 | 32.8965
8.3438 | 12745 | 221.863 | 33.279
8.3542 | 13597 | 224.497 | 33.9482
8.3646 | 14171 | 229.249 | 34.8338
8.375 | 14171 | 229.249 | 34.8338
8.3854 | 17637 | 242.485 | 38.5688
8.3958 | 17635 | 264.33 | 45.2445
8.4062 | 22461 | 298.601 | 52.6706
8.4167 | 26276 | 337.077 | 59.3141
8.4271 | 25598 | 375.399 | 67.5693
8.4375 | 27780 | 413.696 | 73.7548
8.4479 | 29551 | 452.36 | 79.3185
8.4583 | 31861 | 486.992 | 82.7013
8.4688 | 32171 | 512.038 | 83.4993
8.4792 | 32180 | 527.073 | 80.6565
8.4896 | 31869 | 534.619 | 75.81
8.5 | 28047 | 530.642 | 72.7503
8.5104 | 26690 | 514.116 | 66.1859
8.5208 | 25572 | 503.532 | 63.0469
8.5312 | 25496 | 496.76 | 61.0328
8.5417 | 22401 | 482.346 | 58.5822
8.5521 | 26555 | 487.172 | 58.9774
8.5625 | 25905 | 488.184 | 58.195
8.5729 | 24310 | 483.723 | 57.1044
8.5833 | 23404 | 478.181 | 56.8374
8.5938 | 20560 | 463.806 | 54.995
8.6042 | 18732 | 443.922 | 53.4856
8.6146 | 25320 | 451.218 | 53.7971
8.625 | 25320 | 451.218 | 53.7971
8.6354 | 23046 | 445.711 | 52.6887
8.6458 | 21357 | 436.331 | 51.9174
8.6562 | 22487 | 433.833 | 52.4168
8.6667 | 18221 | 417.816 | 51.3897
8.6771 | 17442 | 402.053 | 50.2781
8.6875 | 19246 | 397.534 | 50.6766
8.6979 | 19197 | 394.731 | 51.5771
8.7083 | 19637 | 392.367 | 51.4381
8.7188 | 19014 | 386.358 | 50.3783
8.7292 | 18480 | 376.467 | 48.5387
8.7396 | 18208 | 368.187 | 47.8773
8.75 | 18547 | 364.455 | 47.7202
8.7604 | 18670 | 363.481 | 49.5326
8.7708 | 18654 | 364.512 | 50.6437
8.7812 | 23137 | 376.541 | 53.2088
8.7917 | 22509 | 383.808 | 53.4958
8.8021 | 22031 | 388.158 | 51.2442
8.8125 | 22489 | 398.101 | 53.6977
8.8229 | 18876 | 391.676 | 52.9122
8.8333 | 20674 | 394.139 | 53.8248
8.8438 | 24145 | 409.78 | 57.1672
8.8542 | 22518 | 417.213 | 59.166
8.8646 | 22803 | 423.276 | 60.1623
8.875 | 22803 | 423.276 | 60.1623
8.8854 | 21780 | 426.09 | 61.6272
8.8958 | 19067 | 420.05 | 61.441
8.9062 | 26211 | 439.142 | 63.4727
8.9167 | 24096 | 445.193 | 63.0497
8.9271 | 23071 | 445.77 | 63.1375
8.9375 | 22388 | 443.7 | 62.7881
8.9479 | 17483 | 424.981 | 60.6968
8.9583 | 25814 | 438.815 | 62.1559
8.9688 | 23248 | 438.995 | 60.8938
8.9792 | 24098 | 440.224 | 59.4942
8.9896 | 22402 | 435.94 | 57.6494
9 | 19962 | 424.663 | 55.7783
9.0104 | 18618 | 398.5 | 53.4007
9.0208 | 19046 | 393.304 | 54.0075
9.0312 | 23433 | 403.839 | 55.8545
9.0417 | 22011 | 408.218 | 57.4939
9.0521 | 23310 | 417.413 | 60.3045
9.0625 | 23158 | 425.681 | 63.6883
9.0729 | 15122 | 402.222 | 61.2693
9.0833 | 15319 | 383.34 | 59.1363
9.0938 | 15342 | 368.602 | 57.8635
9.1042 | 14751 | 351.82 | 54.5865
9.1146 | 14287 | 339.78 | 54.1525
9.125 | 14287 | 339.78 | 54.1525
9.1354 | 12478 | 319.354 | 49.8604
9.1458 | 12477 | 306.971 | 47.074
9.1562 | 11347 | 288.387 | 42.9496
9.1667 | 11037 | 272.158 | 39.5317
9.1771 | 10473 | 258.031 | 37.3391
9.1875 | 10000 | 244.708 | 35.3368
9.1979 | 11258 | 236.118 | 32.9808
9.2083 | 10436 | 228.58 | 32.7737
9.2188 | 10976 | 223.715 | 32.7521
9.2292 | 11250 | 219.452 | 32.5682
9.2396 | 11740 | 217.583 | 32.4339
9.25 | 11562 | 214.543 | 32.1927
9.2604 | 12578 | 214.146 | 32.0666
9.2708 | 11399 | 210.837 | 31.773
9.2812 | 11448 | 208.333 | 31.3923
9.2917 | 12090 | 208.104 | 31.2846
9.3021 | 12429 | 209.075 | 31.3436
9.3125 | 11500 | 207.25 | 31.3023
9.3229 | 11717 | 206.549 | 31.5964
9.3333 | 11751 | 206.058 | 32.0027
9.3438 | 11489 | 205.392 | 32.3337
9.3542 | 12859 | 208.553 | 33.0549
9.3646 | 12350 | 210.671 | 33.7288
9.375 | 12350 | 210.671 | 33.7288
9.3854 | 12194 | 215.612 | 36.7541
9.3958 | 15329 | 235.446 | 43.5038
9.4062 | 22901 | 274.793 | 51.343
9.4167 | 23690 | 308.419 | 57.3951
9.4271 | 24749 | 348.238 | 65.8921
9.4375 | 27249 | 388.599 | 72.1992
9.4479 | 29504 | 430.668 | 78.0019
9.4583 | 31868 | 471.119 | 81.728
9.4688 | 32126 | 501.093 | 82.8186
9.4792 | 31909 | 519.703 | 80.1566
9.4896 | 31927 | 531.491 | 75.6279
9.5 | 31719 | 540.931 | 74.0525
9.5104 | 27039 | 534.318 | 67.4458
9.5208 | 25844 | 522.549 | 64.2126
9.5312 | 25174 | 510.637 | 61.7853
9.5417 | 24783 | 502.414 | 60.1624
9.5521 | 24444 | 495.288 | 59.0782
9.5625 | 22762 | 484.346 | 57.4217
9.5729 | 24940 | 484.59 | 57.265
9.5833 | 24113 | 481.797 | 57.1684
9.5938 | 23320 | 476.538 | 56.182
9.6042 | 22247 | 467.756 | 55.3934
9.6146 | 21875 | 456.89 | 53.5688
9.625 | 21875 | 456.89 | 53.5688
9.6354 | 21863 | 447.211 | 52.5853
9.6458 | 21236 | 438.046 | 51.995
9.6562 | 21473 | 432.225 | 52.1678
9.6667 | 20822 | 426.133 | 52.244
9.6771 | 20463 | 420.443 | 51.7382
9.6875 | 20034 | 415.884 | 51.8146
9.6979 | 19328 | 411.428 | 52.5267
9.7083 | 18928 | 403.512 | 51.9631
9.7188 | 18510 | 394.292 | 50.7516
9.7292 | 18319 | 383.021 | 48.8803
9.7396 | 18224 | 375.88 | 48.3045
9.75 | 19106 | 372.828 | 48.2564
9.7604 | 21604 | 388.29 | 51.3019
9.7708 | 22228 | 395.84 | 52.869
9.7812 | 21169 | 395.293 | 54.0189
9.7917 | 19849 | 391.428 | 53.5743
9.8021 | 17451 | 380.798 | 50.2302
9.8125 | 18335 | 380.482 | 52.158
9.8229 | 22018 | 389.449 | 53.2013
9.8333 | 23369 | 400.713 | 54.563
9.8438 | 23270 | 411.344 | 57.1361
9.8542 | 25050 | 426.904 | 60.0863
9.8646 | 21540 | 426.313 | 60.1561
9.875 | 21540 | 426.313 | 60.1561
9.8854 | 19321 | 420.609 | 60.9717
9.8958 | 21190 | 423.674 | 61.9397
9.9062 | 26591 | 443.175 | 63.7658
9.9167 | 24225 | 448.869 | 63.2819
9.9271 | 23902 | 451.657 | 63.6021
9.9375 | 24339 | 455.04 | 63.7372
9.9479 | 21529 | 447.472 | 62.5475
9.9583 | 26978 | 460.136 | 63.5916
9.9688 | 25693 | 464.394 | 62.7504
9.9792 | 24779 | 462.814 | 60.9135
9.9896 | 24086 | 460.173 | 59.3084
10 | 23308 | 455.71 | 58.0596
10.0104 | 21014 | 433.315 | 55.7004
10.0208 | 19118 | 405.874 | 54.7168
10.0312 | 18847 | 406.265 | 55.3458
10.0417 | 18509 | 402.748 | 56.6962
10.0521 | 17886 | 400.461 | 58.5891
10.0625 | 17445 | 399.241 | 61.4037
10.0729 | 16858 | 392.979 | 60.9977
10.0833 | 16116 | 396.435 | 59.9493
10.0938 | 16206 | 383.436 | 58.775
10.1042 | 15965 | 368.325 | 55.6244
10.1146 | 14494 | 359.929 | 55.2555
10.125 | 14494 | 359.929 | 55.2555
10.1354 | 13423 | 344.187 | 51.2796
10.1458 | 12660 | 333.85 | 48.5108
10.1562 | 12059 | 317.058 | 44.5214
10.1667 | 11453 | 300.831 | 41.0666
10.1771 | 12083 | 286.664 | 38.9758
10.1875 | 11554 | 272.898 | 36.9315
10.1979 | 11875 | 262.401 | 34.405
10.2083 | 13101 | 254.173 | 34.3194
10.2188 | 12323 | 248.221 | 34.1346
10.2292 | 13271 | 246.103 | 34.118
10.2396 | 13614 | 242.043 | 33.8589
10.25 | 13604 | 240.755 | 33.7206
10.2604 | 12408 | 240.457 | 33.4415
10.2708 | 11767 | 236.243 | 33.1271
10.2812 | 12006 | 233.013 | 32.7229
10.2917 | 11805 | 228.517 | 32.3364
10.3021 | 11951 | 225.931 | 32.1976
10.3125 | 12317 | 223.087 | 32.1857
10.3229 | 12825 | 221.208 | 32.4389
10.3333 | 12800 | 220.628 | 32.8368
10.3438 | 12600 | 221.957 | 33.2747
10.3542 | 13408 | 222.805 | 33.845
10.3646 | 13952 | 223.935 | 34.5356
10.375 | 13952 | 223.935 | 34.5356
10.3854 | 17235 | 230.837 | 37.9001
10.3958 | 17233 | 245.177 | 44.1624
10.4062 | 21804 | 265.157 | 50.7095
10.4167 | 25418 | 284.426 | 56.145
10.4271 | 24776 | 322.005 | 64.367
10.4375 | 26842 | 362.795 | 70.6261
10.4479 | 28519 | 395.642 | 75.7771
10.4583 | 30707 | 427.852 | 78.9243
10.4688 | 31000 | 456.023 | 79.8884
10.4792 | 31009 | 478.98 | 77.5175
10.4896 | 30713 | 495.397 | 73.2112
10.5 | 27093 | 509.635 | 71.3304
10.5104 | 25808 | 516.967 | 66.1931
10.5208 | 24748 | 510.469 | 63.3037
10.5312 | 24677 | 503.054 | 61.2522
10.5417 | 21745 | 495.89 | 59.239
10.5521 | 25678 | 493.274 | 59.1811
10.5625 | 25062 | 480.696 | 57.6101
10.5729 | 23552 | 487.077 | 57.1669
10.5833 | 22693 | 489.366 | 57.3575
10.5938 | 20001 | 485.226 | 56.1043
10.6042 | 18269 | 478.271 | 55.3134
10.6146 | 24508 | 460.124 | 54.1847
10.625 | 24508 | 460.124 | 54.1847
10.6354 | 22354 | 437.134 | 52.0876
10.6458 | 20755 | 445.688 | 52.3517
10.6562 | 21824 | 442.89 | 52.8289
10.6667 | 17785 | 435.839 | 52.3177
10.6771 | 17047 | 434.983 | 52.0261
10.6875 | 18755 | 420.746 | 51.8986
10.6979 | 18708 | 407.608 | 52.2271
10.7083 | 19125 | 400.63 | 51.8303
10.7188 | 18535 | 392.776 | 50.6708
10.7292 | 18029 | 386.203 | 49.018
10.7396 | 17772 | 380.609 | 48.5057
10.75 | 18093 | 374.177 | 48.2
10.7604 | 18209 | 367.506 | 49.6982
10.7708 | 18193 | 368.129 | 50.7874
10.7812 | 22437 | 365.306 | 52.4771
10.7917 | 21842 | 363.401 | 52.2469
10.8021 | 21390 | 376.101 | 50.4752
10.8125 | 21824 | 387.915 | 53.0275
10.8229 | 18403 | 393.24 | 52.9362
10.8333 | 20104 | 400.066 | 54.082
10.8438 | 23390 | 396.287 | 56.2854
10.8542 | 21850 | 401.222 | 58.1622
10.8646 | 22120 | 415.236 | 59.6067
10.875 | 22120 | 415.236 | 59.6067
10.8854 | 21151 | 421.553 | 61.2805
10.8958 | 18582 | 428.336 | 61.8339
10.9062 | 25345 | 429.74 | 62.7953
10.9167 | 23343 | 421.569 | 61.576
10.9271 | 22372 | 438.576 | 62.6222
10.9375 | 21725 | 442.859 | 62.641
10.9479 | 17083 | 442.424 | 61.5958
10.9583 | 24968 | 439.346 | 62.0609
10.9688 | 22540 | 420.363 | 59.7205
10.9792 | 23343 | 432.824 | 58.9533
10.9896 | 21738 | 432.716 | 57.3657
11 | 19429 | 435.736 | 56.3188
11.0104 | 18156 | 418.73 | 54.4544
11.0208 | 18561 | 406.677 | 54.6824
11.0312 | 22713 | 398.89 | 55.4699
11.0417 | 21366 | 396.066 | 56.7138
11.0521 | 22596 | 409.429 | 59.7438
11.0625 | 22452 | 415.684 | 63.0135
11.0729 | 14847 | 421.931 | 62.2922
11.0833 | 15033 | 423.196 | 61.2461
11.0938 | 15055 | 397.158 | 59.3662
11.1042 | 14496 | 376.33 | 55.8715
11.1146 | 14056 | 363.267 | 55.3816
11.125 | 14056 | 363.267 | 55.3816
11.1354 | 12345 | 342.654 | 51.0731
11.1458 | 12344 | 331.926 | 48.3744
11.1562 | 11274 | 315.622 | 44.3627
11.1667 | 10981 | 298.828 | 40.915
11.1771 | 10448 | 282.636 | 38.6115
11.1875 | 10000 | 268.347 | 36.5567
11.1979 | 11190 | 253.645 | 33.8895
11.2083 | 10412 | 242.497 | 33.4925
11.2188 | 10923 | 236.877 | 33.4322
11.2292 | 11182 | 228.643 | 33.0422
11.2396 | 11646 | 223.762 | 32.7508
11.25 | 11478 | 219.443 | 32.4442
11.2604 | 12439 | 214.596 | 32.0814
11.2708 | 11323 | 213.56 | 31.91
11.2812 | 11370 | 213.733 | 31.6694
11.2917 | 11977 | 210.569 | 31.4074
11.3021 | 12298 | 208.554 | 31.3076
11.3125 | 11419 | 208.637 | 31.3696
11.3229 | 11624 | 209.623 | 31.751
11.3333 | 11656 | 207.83 | 32.0901
11.3438 | 11409 | 207.518 | 32.4399
11.3542 | 12704 | 207.316 | 32.9796
11.3646 | 12223 | 207.473 | 33.553
11.375 | 12223 | 207.473 | 33.553
11.3854 | 12076 | 214.902 | 36.7102
11.3958 | 15040 | 226.609 | 43.0091
11.4062 | 22202 | 238.297 | 49.2052
11.4167 | 22948 | 255.559 | 54.2938
11.4271 | 23950 | 298.211 | 62.9163
11.4375 | 26314 | 334.153 | 68.8839
11.4479 | 28447 | 368.497 | 74.1426
11.4583 | 30682 | 402.767 | 77.3936
11.4688 | 30926 | 434.341 | 78.5554
11.4792 | 30720 | 463.112 | 76.5077
11.4896 | 30737 | 484.454 | 72.5487
11.5 | 30540 | 502.265 | 71.479
11.5104 | 26113 | 527.245 | 66.8543
11.5208 | 24983 | 533.06 | 64.6641
11.5312 | 24349 | 523.24 | 62.3649
11.5417 | 23979 | 514.893 | 60.7385
11.5521 | 23658 | 507.141 | 59.6223
11.5625 | 22068 | 500.749 | 58.2353
11.5729 | 24127 | 495.185 | 57.7369
11.5833 | 23345 | 485.528 | 57.2504
11.5938 | 22595 | 486.089 | 56.6056
11.6042 | 21580 | 481.879 | 56.0848
11.6146 | 21228 | 472.845 | 54.3665
11.625 | 21228 | 472.845 | 54.3665
11.6354 | 21217 | 460.952 | 53.2605
11.6458 | 20623 | 451.353 | 52.65
11.6562 | 20848 | 444.386 | 52.7577
11.6667 | 20232 | 437.551 | 52.796
11.6771 | 19893 | 433.371 | 52.3779
11.6875 | 19487 | 429.056 | 52.4705
11.6979 | 18819 | 425.985 | 53.2629
11.7083 | 18441 | 418.967 | 52.7517
11.7188 | 18045 | 409.461 | 51.5261
11.7292 | 17864 | 397.339 | 49.6093
11.7396 | 17775 | 388.533 | 48.9427
11.75 | 18608 | 380.723 | 48.6296
11.7604 | 20969 | 375.871 | 50.5147
11.7708 | 21559 | 387.657 | 52.3128
11.7812 | 20558 | 390.1 | 53.6433
11.7917 | 19310 | 394.71 | 53.6845
11.8021 | 17043 | 394.839 | 50.9452
11.8125 | 17878 | 395.529 | 52.9297
11.8229 | 21360 | 385.882 | 52.9125
11.8333 | 22636 | 382.453 | 53.4169
11.8438 | 22542 | 394.058 | 56.0453
11.8542 | 24225 | 407.791 | 58.8591
11.8646 | 20907 | 416.799 | 59.5274
11.875 | 20907 | 416.799 | 59.5274
11.8854 | 18809 | 431.235 | 61.4901
11.8958 | 20576 | 431.369 | 62.2881
11.9062 | 25680 | 424.259 | 62.5216
11.9167 | 23444 | 425.189 | 61.7995
11.9271 | 23139 | 442.605 | 62.9656
11.9375 | 23551 | 446.529 | 63.1246
11.9479 | 20895 | 448.304 | 62.498
11.9583 | 26044 | 450.677 | 62.8879
11.9688 | 24830 | 442.837 | 61.3545
11.9792 | 23966 | 454.13 | 60.2793
11.9896 | 23311 | 458.097 | 59.0631
12 | 22576 | 458.31 | 58.0896
12.0104 | 20408 | 449.755 | 56.5323
12.0208 | 18616 | 399.989 | 54.3197
12.0312 | 18359 | 394.865 | 54.6464
12.0417 | 18040 | 391.764 | 56.0247
12.0521 | 17452 | 388.442 | 57.8703
12.0625 | 17034 | 398.901 | 61.3299
12.0729 | 16480 | 388.491 | 60.7043
12.0833 | 15778 | 375.328 | 58.7609
12.0938 | 15863 | 365.261 | 57.7455
12.1042 | 15636 | 353.352 | 54.773
12.1146 | 14246 | 341.704 | 54.2506
12.125 | 14246 | 341.704 | 54.2506
12.1354 | 13234 | 320.789 | 50.0168
12.1458 | 12513 | 308.975 | 47.1829
12.1562 | 11946 | 292.417 | 43.2167
12.1667 | 11373 | 276.711 | 39.7989
12.1771 | 11968 | 266.792 | 37.922
12.1875 | 11468 | 256.391 | 36.0607
12.1979 | 11771 | 247.469 | 33.6141
12.2083 | 12929 | 246.049 | 33.8758
12.2188 | 12195 | 242.005 | 33.7971
12.2292 | 13090 | 240.775 | 33.8217
12.2396 | 13414 | 241.083 | 33.7925
12.25 | 13404 | 240.418 | 33.687
12.2604 | 12275 | 233.437 | 33.0618
12.2708 | 11669 | 228.794 | 32.7299
12.2812 | 11895 | 225.718 | 32.3323
12.2917 | 11705 | 222.563 | 32.0183
12.3021 | 11843 | 220.665 | 31.9139
12.3125 | 12189 | 220.054 | 32.0175
12.3229 | 12669 | 220.996 | 32.417
12.3333 | 12645 | 221.556 | 32.8755
12.3438 | 12456 | 221.863 | 33.2595
12.3542 | 13219 | 224.498 | 33.9222
12.3646 | 13732 | 229.249 | 34.8031
12.375 | 13732 | 229.249 | 34.8031
12.3854 | 16832 | 242.485 | 38.5095
12.3958 | 16830 | 264.33 | 45.1813
12.4062 | 21148 | 298.6 | 52.554
12.4167 | 24560 | 337.077 | 59.1388
12.4271 | 23953 | 375.399 | 67.3838
12.4375 | 25904 | 413.696 | 73.5202
12.4479 | 27488 | 452.36 | 79.0333
12.4583 | 29553 | 486.992 | 82.3513
12.4688 | 29829 | 512.038 | 83.1167
12.4792 | 29837 | 527.074 | 80.2506
12.4896 | 29558 | 534.619 | 75.3918
12.5 | 26139 | 530.642 | 72.4019
12.5104 | 24925 | 514.117 | 65.8659
12.5208 | 23924 | 503.532 | 62.7521
12.5312 | 23857 | 496.759 | 60.7403
12.5417 | 21088 | 482.346 | 58.3554
12.5521 | 24802 | 487.172 | 58.6697
12.5625 | 24220 | 488.185 | 57.8984
12.5729 | 22794 | 483.723 | 56.8406
12.5833 | 21983 | 478.182 | 56.5945
12.5938 | 19441 | 463.805 | 54.8111
12.6042 | 17806 | 443.922 | 53.3417
12.6146 | 23695 | 451.218 | 53.5368
12.625 | 23695 | 451.218 | 53.5368
12.6354 | 21662 | 445.711 | 52.4682
12.6458 | 20152 | 436.331 | 51.7294
12.6562 | 21161 | 433.833 | 52.2112
12.6667 | 17348 | 417.816 | 51.2607
12.6771 | 16651 | 402.052 | 50.1672
12.6875 | 18264 | 397.534 | 50.5418
12.6979 | 18220 | 394.731 | 51.4456
12.7083 | 18613 | 392.367 | 51.3013
12.7188 | 18056 | 386.359 | 50.2523
12.7292 | 17578 | 376.468 | 48.4223
12.7396 | 17335 | 368.187 | 47.7673
12.75 | 17638 | 364.455 | 47.6068
12.7604 | 17747 | 363.481 | 49.4192
12.7708 | 17733 | 364.512 | 50.5312
12.7812 | 21738 | 376.541 | 53.0298
12.7917 | 21176 | 383.808 | 53.3209
12.8021 | 20749 | 388.158 | 51.0733
12.8125 | 21158 | 398.101 | 53.517
12.8229 | 17930 | 391.676 | 52.7868
12.8333 | 19535 | 394.139 | 53.6733
12.8438 | 22636 | 409.78 | 56.9581
12.8542 | 21182 | 417.213 | 58.9787
12.8646 | 21436 | 423.276 | 59.968
12.875 | 21436 | 423.276 | 59.968
12.8854 | 20522 | 426.09 | 61.4483
12.8958 | 18098 | 420.05 | 61.307
12.9062 | 24479 | 439.141 | 63.2192
12.9167 | 22590 | 445.192 | 62.8253
12.9271 | 21673 | 445.769 | 62.9284
12.9375 | 21063 | 443.699 | 62.5903
12.9479 | 16683 | 424.981 | 60.5834
12.9583 | 24122 | 438.815 | 61.9038
12.9688 | 21831 | 438.995 | 60.6811
12.9792 | 22589 | 440.223 | 59.2644
12.9896 | 21074 | 435.94 | 57.4484
13 | 18895 | 424.663 | 55.6212
13.0104 | 16990 | 331.66 | 49.5169
13.0208 | 15964 | 328.748 | 50.0852
13.0312 | 15806 | 334.966 | 51.0516
13.0417 | 15610 | 338.529 | 52.819
13.0521 | 15247 | 345.206 | 55.2486
13.0625 | 14989 | 351.794 | 58.5205
13.0729 | 14647 | 338.589 | 57.7894
13.0833 | 14212 | 326.681 | 55.9646
13.0938 | 14266 | 317.322 | 54.9879
13.1042 | 14126 | 305.764 | 52.0524
13.1146 | 13264 | 298.654 | 51.8564
13.125 | 13264 | 298.654 | 51.8564
13.1354 | 12636 | 283.361 | 47.9766
13.1458 | 12189 | 276.608 | 45.4481
13.1562 | 11836 | 264.125 | 41.7228
13.1667 | 11481 | 253.269 | 38.5838
13.1771 | 11851 | 244.348 | 36.736
13.1875 | 11540 | 235.974 | 34.9997
13.1979 | 11729 | 229.963 | 32.694
13.2083 | 12450 | 225.821 | 32.7715
13.2188 | 11994 | 223.206 | 32.7946
13.2292 | 12552 | 220.635 | 32.7174
13.2396 | 12755 | 219.725 | 32.6135
13.25 | 12749 | 217.828 | 32.4437
13.2604 | 12046 | 217.63 | 32.2152
13.2708 | 11668 | 215.643 | 32.0419
13.2812 | 11810 | 214.125 | 31.7186
13.2917 | 11692 | 213.966 | 31.5665
13.3021 | 11778 | 214.649 | 31.5945
13.3125 | 11994 | 213.705 | 31.6718
13.3229 | 12294 | 213.435 | 31.9941
13.3333 | 12280 | 213.269 | 32.4142
13.3438 | 12162 | 213.185 | 32.7838
13.3542 | 12640 | 215.238 | 33.394
13.3646 | 12962 | 217.104 | 34.1071
13.375 | 12962 | 217.104 | 34.1071
13.3854 | 14903 | 221.997 | 37.2643
13.3958 | 14903 | 238.126 | 43.6203
13.4062 | 17608 | 265.681 | 50.4294
13.4167 | 19748 | 288.665 | 55.9379
13.4271 | 19370 | 317.918 | 63.6591
13.4375 | 20596 | 345.785 | 69.0288
13.4479 | 21592 | 374.034 | 73.7682
13.4583 | 22891 | 399.399 | 76.3136
13.4688 | 23068 | 416.261 | 76.5079
13.4792 | 23077 | 424.12 | 73.1623
13.4896 | 22905 | 426.867 | 68.0025
13.5 | 20762 | 429.12 | 65.6899
13.5104 | 20005 | 419.678 | 59.6768
13.5208 | 19379 | 410.599 | 56.7522
13.5312 | 19339 | 401.486 | 54.6182
13.5417 | 17601 | 395.896 | 52.9966
13.5521 | 19939 | 391.3 | 52.4411
13.5625 | 19576 | 384.906 | 51.3064
13.5729 | 18681 | 385.221 | 50.6582
13.5833 | 18173 | 384.074 | 50.7412
13.5938 | 16574 | 381.34 | 49.8416
13.6042 | 15545 | 376.127 | 49.3228
13.6146 | 19259 | 368.552 | 48.2172
13.625 | 19259 | 368.552 | 48.2172
13.6354 | 17980 | 361.503 | 47.2342
13.6458 | 17030 | 355.44 | 46.8131
13.6562 | 17669 | 351.76 | 47.1508
13.6667 | 15264 | 348.452 | 47.2093
13.6771 | 14826 | 345.533 | 46.873
13.6875 | 15846 | 343.854 | 47.299
13.6979 | 15819 | 342.747 | 48.3049
13.7083 | 16069 | 338.081 | 48.0123
13.7188 | 15719 | 332.083 | 47.0043
13.7292 | 15418 | 323.696 | 45.2919
13.7396 | 15266 | 319.073 | 44.8557
13.75 | 15459 | 316.907 | 44.7646
13.7604 | 15531 | 327.252 | 47.1876
13.7708 | 15524 | 332.832 | 48.5483
13.7812 | 18062 | 332.175 | 50.1097
13.7917 | 17708 | 329.891 | 49.8971
13.8021 | 17440 | 323.65 | 47.0883
13.8125 | 17701 | 325.33 | 49.0408
13.8229 | 15656 | 330.898 | 49.1948
13.8333 | 16676 | 338.019 | 50.2296
13.8438 | 18646 | 345.666 | 52.8482
13.8542 | 17726 | 356.327 | 55.141
13.8646 | 17889 | 356.764 | 55.7966
13.875 | 17889 | 356.764 | 55.7966
13.8854 | 17311 | 354.572 | 57.066
13.8958 | 15773 | 357.441 | 57.5921
13.9062 | 19830 | 369.355 | 58.6288
13.9167 | 18631 | 372.87 | 58.2234
13.9271 | 18051 | 374.18 | 58.434
13.9375 | 17665 | 375.615 | 58.3352
13.9479 | 14880 | 370.46 | 57.3949
13.9583 | 19617 | 376.895 | 57.7698
13.9688 | 18161 | 378.534 | 56.7891
13.9792 | 18646 | 376.09 | 55.1058
13.9896 | 17683 | 373.579 | 53.5013
14 | 16297 | 370.197 | 52.2749

## Rain Influent
Raun Influent
Time | Flow rate | Total COD | Total Kjeldahl nitrogen (TKN)
d | m3/d | g COD/m3 | g N/m3
0 | 18446 | 381.19 | 54.4256
0.010417 | 18446 | 381.19 | 54.4256
0.020833 | 18446 | 381.19 | 54.4256
0.03125 | 18446 | 381.19 | 54.4256
0.041667 | 18446 | 381.19 | 54.4256
0.052083 | 18446 | 381.19 | 54.4256
0.0625 | 18446 | 381.19 | 54.4256
0.072917 | 18446 | 381.19 | 54.4256
0.083333 | 18446 | 381.19 | 54.4256
0.09375 | 18446 | 381.19 | 54.4256
0.10417 | 18446 | 381.19 | 54.4256
0.11458 | 18446 | 381.19 | 54.4256
0.125 | 18446 | 381.19 | 54.4256
0.13542 | 18446 | 381.19 | 54.4256
0.14583 | 18446 | 381.19 | 54.4256
0.15625 | 18446 | 381.19 | 54.4256
0.16667 | 18446 | 381.19 | 54.4256
0.17708 | 18446 | 381.19 | 54.4256
0.1875 | 18446 | 381.19 | 54.4256
0.19792 | 18446 | 381.19 | 54.4256
0.20833 | 18446 | 381.19 | 54.4256
0.21875 | 18446 | 381.19 | 54.4256
0.22917 | 18446 | 381.19 | 54.4256
0.23958 | 18446 | 381.19 | 54.4256
0.25 | 18446 | 381.19 | 54.4256
0.26042 | 18446 | 381.19 | 54.4256
0.27083 | 18446 | 381.19 | 54.4256
0.28125 | 18446 | 381.19 | 54.4256
0.29167 | 18446 | 381.19 | 54.4256
0.30208 | 18446 | 381.19 | 54.4256
0.3125 | 18446 | 381.19 | 54.4256
0.32292 | 18446 | 381.19 | 54.4256
0.33333 | 18446 | 381.19 | 54.4256
0.34375 | 18446 | 381.19 | 54.4256
0.35417 | 18446 | 381.19 | 54.4256
0.36458 | 18446 | 381.19 | 54.4256
0.375 | 18446 | 381.19 | 54.4256
0.38542 | 18446 | 381.19 | 54.4256
0.39583 | 18446 | 381.19 | 54.4256
0.40625 | 18446 | 381.19 | 54.4256
0.41667 | 18446 | 381.19 | 54.4256
0.42708 | 18446 | 381.19 | 54.4256
0.4375 | 18446 | 381.19 | 54.4256
0.44792 | 18446 | 381.19 | 54.4256
0.45833 | 18446 | 381.19 | 54.4256
0.46875 | 18446 | 381.19 | 54.4256
0.47917 | 18446 | 381.19 | 54.4256
0.48958 | 18446 | 381.19 | 54.4256
0.5 | 18446 | 381.19 | 54.4256
0.51042 | 18446 | 381.19 | 54.4256
0.52083 | 18446 | 381.19 | 54.4256
0.53125 | 18446 | 381.19 | 54.4256
0.54167 | 18446 | 381.19 | 54.4256
0.55208 | 18446 | 381.19 | 54.4256
0.5625 | 18446 | 381.19 | 54.4256
0.57292 | 18446 | 381.19 | 54.4256
0.58333 | 18446 | 381.19 | 54.4256
0.59375 | 18446 | 381.19 | 54.4256
0.60417 | 18446 | 381.19 | 54.4256
0.61458 | 18446 | 381.19 | 54.4256
0.625 | 18446 | 381.19 | 54.4256
0.63542 | 18446 | 381.19 | 54.4256
0.64583 | 18446 | 381.19 | 54.4256
0.65625 | 18446 | 381.19 | 54.4256
0.66667 | 18446 | 381.19 | 54.4256
0.67708 | 18446 | 381.19 | 54.4256
0.6875 | 18446 | 381.19 | 54.4256
0.69792 | 18446 | 381.19 | 54.4256
0.70833 | 18446 | 381.19 | 54.4256
0.71875 | 18446 | 381.19 | 54.4256
0.72917 | 18446 | 381.19 | 54.4256
0.73958 | 18446 | 381.19 | 54.4256
0.75 | 18446 | 381.19 | 54.4256
0.76042 | 18446 | 381.19 | 54.4256
0.77083 | 18446 | 381.19 | 54.4256
0.78125 | 18446 | 381.19 | 54.4256
0.79167 | 18446 | 381.19 | 54.4256
0.80208 | 18446 | 381.19 | 54.4256
0.8125 | 18446 | 381.19 | 54.4256
0.82292 | 18446 | 381.19 | 54.4256
0.83333 | 18446 | 381.19 | 54.4256
0.84375 | 18446 | 381.19 | 54.4256
0.85417 | 18446 | 381.19 | 54.4256
0.86458 | 18446 | 381.19 | 54.4256
0.875 | 18446 | 381.19 | 54.4256
0.88542 | 18446 | 381.19 | 54.4256
0.89583 | 18446 | 381.19 | 54.4256
0.90625 | 18446 | 381.19 | 54.4256
0.91667 | 18446 | 381.19 | 54.4256
0.92708 | 18446 | 381.19 | 54.4256
0.9375 | 18446 | 381.19 | 54.4256
0.94792 | 18446 | 381.19 | 54.4256
0.95833 | 18446 | 381.19 | 54.4256
0.96875 | 18446 | 381.19 | 54.4256
0.97917 | 18446 | 381.19 | 54.4256
0.98958 | 18446 | 381.19 | 54.4256
1 | 18446 | 381.19 | 54.4256
1.0104 | 21477 | 407.888 | 54.4476
1.0208 | 21474 | 405.876 | 54.2133
1.0312 | 19620 | 399.989 | 54.459
1.0417 | 19334 | 394.865 | 54.7792
1.0521 | 18978 | 391.764 | 56.1501
1.0625 | 18321 | 388.441 | 57.984
1.0729 | 17855 | 398.902 | 61.4396
1.0833 | 17237 | 388.491 | 60.8017
1.0938 | 16453 | 375.328 | 58.8446
1.1042 | 16548 | 365.261 | 57.828
1.1146 | 16295 | 353.352 | 54.8502
1.125 | 14743 | 341.929 | 54.3289
1.1354 | 13613 | 320.789 | 50.0572
1.1458 | 12807 | 308.975 | 47.2126
1.1562 | 12173 | 292.417 | 43.2385
1.1667 | 11533 | 276.711 | 39.8134
1.1771 | 12198 | 266.791 | 37.9419
1.1875 | 11640 | 256.39 | 36.0749
1.1979 | 11978 | 247.469 | 33.6307
1.2083 | 13272 | 246.049 | 33.9029
1.2188 | 12452 | 242.006 | 33.817
1.2292 | 13453 | 240.775 | 33.8495
1.2396 | 13815 | 241.083 | 33.8232
1.25 | 13803 | 240.417 | 33.7176
1.2604 | 12514 | 236.456 | 33.3428
1.2708 | 12542 | 233.436 | 33.0814
1.2812 | 11865 | 228.794 | 32.7439
1.2917 | 12118 | 225.718 | 32.3479
1.3021 | 11906 | 222.562 | 32.032
1.3125 | 12059 | 220.665 | 31.9285
1.3229 | 12446 | 220.054 | 32.0348
1.3333 | 12982 | 220.996 | 32.4383
1.3438 | 12956 | 221.556 | 32.8965
1.3542 | 12745 | 221.863 | 33.279
1.3646 | 13597 | 224.497 | 33.9482
1.375 | 14171 | 229.249 | 34.8338
1.3854 | 17637 | 242.485 | 38.5688
1.3958 | 17635 | 264.33 | 45.2445
1.4062 | 22461 | 298.601 | 52.6706
1.4167 | 26276 | 337.077 | 59.3141
1.4271 | 25598 | 375.399 | 67.5693
1.4375 | 27780 | 413.696 | 73.7548
1.4479 | 29551 | 452.36 | 79.3185
1.4583 | 31861 | 486.992 | 82.7013
1.4688 | 32171 | 512.038 | 83.4993
1.4792 | 32180 | 527.073 | 80.6565
1.4896 | 31869 | 534.619 | 75.81
1.5 | 28047 | 530.642 | 72.7503
1.5104 | 26695 | 523.226 | 69.6174
1.5208 | 26690 | 514.116 | 66.1859
1.5312 | 25572 | 503.532 | 63.0469
1.5417 | 25496 | 496.76 | 61.0328
1.5521 | 22401 | 482.346 | 58.5822
1.5625 | 26555 | 487.172 | 58.9774
1.5729 | 25905 | 488.184 | 58.195
1.5833 | 24310 | 483.723 | 57.1044
1.5938 | 23404 | 478.181 | 56.8374
1.6042 | 20560 | 463.806 | 54.995
1.6146 | 18732 | 443.922 | 53.4856
1.625 | 25320 | 451.218 | 53.7971
1.6354 | 23046 | 445.711 | 52.6887
1.6458 | 21357 | 436.331 | 51.9174
1.6562 | 22487 | 433.833 | 52.4168
1.6667 | 18221 | 417.816 | 51.3897
1.6771 | 17442 | 402.053 | 50.2781
1.6875 | 19246 | 397.534 | 50.6766
1.6979 | 19197 | 394.731 | 51.5771
1.7083 | 19637 | 392.367 | 51.4381
1.7188 | 19014 | 386.358 | 50.3783
1.7292 | 18480 | 376.467 | 48.5387
1.7396 | 18208 | 368.187 | 47.8773
1.75 | 18547 | 364.455 | 47.7202
1.7604 | 18666 | 363.648 | 48.5924
1.7708 | 18670 | 363.481 | 49.5326
1.7812 | 18654 | 364.512 | 50.6437
1.7917 | 23137 | 376.541 | 53.2088
1.8021 | 22509 | 383.808 | 53.4958
1.8125 | 22031 | 388.158 | 51.2442
1.8229 | 22489 | 398.101 | 53.6977
1.8333 | 18876 | 391.676 | 52.9122
1.8438 | 20674 | 394.139 | 53.8248
1.8542 | 24145 | 409.78 | 57.1672
1.8646 | 22518 | 417.213 | 59.166
1.875 | 22803 | 423.276 | 60.1623
1.8854 | 21780 | 426.09 | 61.6272
1.8958 | 19067 | 420.05 | 61.441
1.9062 | 26211 | 439.142 | 63.4727
1.9167 | 24096 | 445.193 | 63.0497
1.9271 | 23071 | 445.77 | 63.1375
1.9375 | 22388 | 443.7 | 62.7881
1.9479 | 17483 | 424.981 | 60.6968
1.9583 | 25814 | 438.815 | 62.1559
1.9688 | 23248 | 438.995 | 60.8938
1.9792 | 24098 | 440.224 | 59.4942
1.9896 | 22402 | 435.94 | 57.6494
2 | 19962 | 424.663 | 55.7783
2.0104 | 18363 | 408.694 | 54.0516
2.0208 | 18618 | 398.5 | 53.4007
2.0312 | 19046 | 393.304 | 54.0075
2.0417 | 23433 | 403.839 | 55.8545
2.0521 | 22011 | 408.218 | 57.4939
2.0625 | 23310 | 417.413 | 60.3045
2.0729 | 23158 | 425.681 | 63.6883
2.0833 | 15122 | 402.222 | 61.2693
2.0938 | 15319 | 383.34 | 59.1363
2.1042 | 15342 | 368.602 | 57.8635
2.1146 | 14751 | 351.82 | 54.5865
2.125 | 14287 | 339.78 | 54.1525
2.1354 | 12478 | 319.354 | 49.8604
2.1458 | 12477 | 306.971 | 47.074
2.1562 | 11347 | 288.387 | 42.9496
2.1667 | 11037 | 272.158 | 39.5317
2.1771 | 10473 | 258.031 | 37.3391
2.1875 | 10000 | 244.708 | 35.3368
2.1979 | 11258 | 236.118 | 32.9808
2.2083 | 10436 | 228.58 | 32.7737
2.2188 | 10976 | 223.715 | 32.7521
2.2292 | 11250 | 219.452 | 32.5682
2.2396 | 11740 | 217.583 | 32.4339
2.25 | 11562 | 214.543 | 32.1927
2.2604 | 12124 | 213.759 | 32.1201
2.2708 | 12578 | 214.146 | 32.0666
2.2812 | 11399 | 210.837 | 31.773
2.2917 | 11448 | 208.333 | 31.3923
2.3021 | 12090 | 208.104 | 31.2846
2.3125 | 12429 | 209.075 | 31.3436
2.3229 | 11500 | 207.25 | 31.3023
2.3333 | 11717 | 206.549 | 31.5964
2.3438 | 11751 | 206.058 | 32.0027
2.3542 | 11489 | 205.392 | 32.3337
2.3646 | 12859 | 208.553 | 33.0549
2.375 | 12350 | 210.671 | 33.7288
2.3854 | 12194 | 215.612 | 36.7541
2.3958 | 15329 | 235.446 | 43.5038
2.4062 | 22901 | 274.793 | 51.343
2.4167 | 23690 | 308.419 | 57.3951
2.4271 | 24749 | 348.238 | 65.8921
2.4375 | 27249 | 388.599 | 72.1992
2.4479 | 29504 | 430.668 | 78.0019
2.4583 | 31868 | 471.119 | 81.728
2.4688 | 32126 | 501.093 | 82.8186
2.4792 | 31909 | 519.703 | 80.1566
2.4896 | 31927 | 531.491 | 75.6279
2.5 | 31719 | 540.931 | 74.0525
2.5104 | 30926 | 545.833 | 71.7675
2.5208 | 27039 | 534.318 | 67.4458
2.5312 | 25844 | 522.549 | 64.2126
2.5417 | 25174 | 510.637 | 61.7853
2.5521 | 24783 | 502.414 | 60.1624
2.5625 | 24444 | 495.288 | 59.0782
2.5729 | 22762 | 484.346 | 57.4217
2.5833 | 24940 | 484.59 | 57.265
2.5938 | 24113 | 481.797 | 57.1684
2.6042 | 23320 | 476.538 | 56.182
2.6146 | 22247 | 467.756 | 55.3934
2.625 | 21875 | 456.89 | 53.5688
2.6354 | 21863 | 447.211 | 52.5853
2.6458 | 21236 | 438.046 | 51.995
2.6562 | 21473 | 432.225 | 52.1678
2.6667 | 20822 | 426.133 | 52.244
2.6771 | 20463 | 420.443 | 51.7382
2.6875 | 20034 | 415.884 | 51.8146
2.6979 | 19328 | 411.428 | 52.5267
2.7083 | 18928 | 403.512 | 51.9631
2.7188 | 18510 | 394.292 | 50.7516
2.7292 | 18319 | 383.021 | 48.8803
2.7396 | 18224 | 375.88 | 48.3045
2.75 | 19106 | 372.828 | 48.2564
2.7604 | 22491 | 383.189 | 50.1831
2.7708 | 21604 | 388.29 | 51.3019
2.7812 | 22228 | 395.84 | 52.869
2.7917 | 21169 | 395.293 | 54.0189
2.8021 | 19849 | 391.428 | 53.5743
2.8125 | 17451 | 380.798 | 50.2302
2.8229 | 18335 | 380.482 | 52.158
2.8333 | 22018 | 389.449 | 53.2013
2.8438 | 23369 | 400.713 | 54.563
2.8542 | 23270 | 411.344 | 57.1361
2.8646 | 25050 | 426.904 | 60.0863
2.875 | 21540 | 426.313 | 60.1561
2.8854 | 19321 | 420.609 | 60.9717
2.8958 | 21190 | 423.674 | 61.9397
2.9062 | 26591 | 443.175 | 63.7658
2.9167 | 24225 | 448.869 | 63.2819
2.9271 | 23902 | 451.657 | 63.6021
2.9375 | 24339 | 455.04 | 63.7372
2.9479 | 21529 | 447.472 | 62.5475
2.9583 | 26978 | 460.136 | 63.5916
2.9688 | 25693 | 464.394 | 62.7504
2.9792 | 24779 | 462.814 | 60.9135
2.9896 | 24086 | 460.173 | 59.3084
3 | 23308 | 455.71 | 58.0596
3.0104 | 21017 | 442.197 | 56.323
3.0208 | 21014 | 433.315 | 55.7004
3.0312 | 19118 | 405.874 | 54.7168
3.0417 | 18847 | 406.265 | 55.3458
3.0521 | 18509 | 402.748 | 56.6962
3.0625 | 17886 | 400.461 | 58.5891
3.0729 | 17445 | 399.241 | 61.4037
3.0833 | 16858 | 392.979 | 60.9977
3.0938 | 16116 | 396.435 | 59.9493
3.1042 | 16206 | 383.436 | 58.775
3.1146 | 15965 | 368.325 | 55.6244
3.125 | 14494 | 359.929 | 55.2555
3.1354 | 13423 | 344.187 | 51.2796
3.1458 | 12660 | 333.85 | 48.5108
3.1562 | 12059 | 317.058 | 44.5214
3.1667 | 11453 | 300.831 | 41.0666
3.1771 | 12083 | 286.664 | 38.9758
3.1875 | 11554 | 272.898 | 36.9315
3.1979 | 11875 | 262.401 | 34.405
3.2083 | 13101 | 254.173 | 34.3194
3.2188 | 12323 | 248.221 | 34.1346
3.2292 | 13271 | 246.103 | 34.118
3.2396 | 13614 | 242.043 | 33.8589
3.25 | 13604 | 240.755 | 33.7206
3.2604 | 12382 | 240.733 | 33.5584
3.2708 | 12408 | 240.457 | 33.4415
3.2812 | 11767 | 236.243 | 33.1271
3.2917 | 12006 | 233.013 | 32.7229
3.3021 | 11805 | 228.517 | 32.3364
3.3125 | 11951 | 225.931 | 32.1976
3.3229 | 12317 | 223.087 | 32.1857
3.3333 | 12825 | 221.208 | 32.4389
3.3438 | 12800 | 220.628 | 32.8368
3.3542 | 12600 | 221.957 | 33.2747
3.3646 | 13408 | 222.805 | 33.845
3.375 | 13952 | 223.935 | 34.5356
3.3854 | 17235 | 230.837 | 37.9001
3.3958 | 17233 | 245.177 | 44.1624
3.4062 | 21804 | 265.157 | 50.7095
3.4167 | 25418 | 284.426 | 56.145
3.4271 | 24776 | 322.005 | 64.367
3.4375 | 26842 | 362.795 | 70.6261
3.4479 | 28519 | 395.642 | 75.7771
3.4583 | 30707 | 427.852 | 78.9243
3.4688 | 31000 | 456.023 | 79.8884
3.4792 | 31009 | 478.98 | 77.5175
3.4896 | 30713 | 495.397 | 73.2112
3.5 | 27093 | 509.635 | 71.3304
3.5104 | 25812 | 520.396 | 69.2898
3.5208 | 25808 | 516.967 | 66.1931
3.5312 | 24748 | 510.469 | 63.3037
3.5417 | 24677 | 503.054 | 61.2522
3.5521 | 21745 | 495.89 | 59.239
3.5625 | 25678 | 493.274 | 59.1811
3.5729 | 25062 | 480.696 | 57.6101
3.5833 | 23552 | 487.077 | 57.1669
3.5938 | 22693 | 489.366 | 57.3575
3.6042 | 20001 | 485.226 | 56.1043
3.6146 | 18269 | 478.271 | 55.3134
3.625 | 24508 | 460.124 | 54.1847
3.6354 | 22354 | 437.134 | 52.0876
3.6458 | 20755 | 445.688 | 52.3517
3.6562 | 21824 | 442.89 | 52.8289
3.6667 | 17785 | 435.839 | 52.3177
3.6771 | 17047 | 434.983 | 52.0261
3.6875 | 18755 | 420.746 | 51.8986
3.6979 | 18708 | 407.608 | 52.2271
3.7083 | 19125 | 400.63 | 51.8303
3.7188 | 18535 | 392.776 | 50.6708
3.7292 | 18029 | 386.203 | 49.018
3.7396 | 17772 | 380.609 | 48.5057
3.75 | 18093 | 374.177 | 48.2
3.7604 | 18205 | 368.454 | 48.8004
3.7708 | 18209 | 367.506 | 49.6982
3.7812 | 18193 | 368.129 | 50.7874
3.7917 | 22437 | 365.306 | 52.4771
3.8021 | 21842 | 363.401 | 52.2469
3.8125 | 21390 | 376.101 | 50.4752
3.8229 | 21824 | 387.915 | 53.0275
3.8333 | 18403 | 393.24 | 52.9362
3.8438 | 20104 | 400.066 | 54.082
3.8542 | 23390 | 396.287 | 56.2854
3.8646 | 21850 | 401.222 | 58.1622
3.875 | 22120 | 415.236 | 59.6067
3.8854 | 21151 | 421.553 | 61.2805
3.8958 | 18582 | 428.336 | 61.8339
3.9062 | 25345 | 429.74 | 62.7953
3.9167 | 23343 | 421.569 | 61.576
3.9271 | 22372 | 438.576 | 62.6222
3.9375 | 21725 | 442.859 | 62.641
3.9479 | 17083 | 442.424 | 61.5958
3.9583 | 24968 | 439.346 | 62.0609
3.9688 | 22540 | 420.363 | 59.7205
3.9792 | 23343 | 432.824 | 58.9533
3.9896 | 21738 | 432.716 | 57.3657
4 | 19429 | 435.736 | 56.3188
4.0104 | 17915 | 430.006 | 55.1644
4.0208 | 18156 | 418.73 | 54.4544
4.0312 | 18561 | 406.677 | 54.6824
4.0417 | 22713 | 398.89 | 55.4699
4.0521 | 21366 | 396.066 | 56.7138
4.0625 | 22596 | 409.429 | 59.7438
4.0729 | 22452 | 415.684 | 63.0135
4.0833 | 14847 | 421.931 | 62.2922
4.0938 | 15033 | 423.196 | 61.2461
4.1042 | 15055 | 397.158 | 59.3662
4.1146 | 14496 | 376.33 | 55.8715
4.125 | 14056 | 363.267 | 55.3816
4.1354 | 12345 | 342.654 | 51.0731
4.1458 | 12344 | 331.926 | 48.3744
4.1562 | 11274 | 315.622 | 44.3627
4.1667 | 10981 | 298.828 | 40.915
4.1771 | 10448 | 282.636 | 38.6115
4.1875 | 10000 | 268.347 | 36.5567
4.1979 | 11190 | 253.645 | 33.8895
4.2083 | 10412 | 242.497 | 33.4925
4.2188 | 10923 | 236.877 | 33.4322
4.2292 | 11182 | 228.643 | 33.0422
4.2396 | 11646 | 223.762 | 32.7508
4.25 | 11478 | 219.443 | 32.4442
4.2604 | 12009 | 217.245 | 32.2967
4.2708 | 12439 | 214.596 | 32.0814
4.2812 | 11323 | 213.56 | 31.91
4.2917 | 11370 | 213.733 | 31.6694
4.3021 | 11977 | 210.569 | 31.4074
4.3125 | 12298 | 208.554 | 31.3076
4.3229 | 11419 | 208.637 | 31.3696
4.3333 | 11624 | 209.623 | 31.751
4.3438 | 11656 | 207.83 | 32.0901
4.3542 | 11409 | 207.518 | 32.4399
4.3646 | 12704 | 207.316 | 32.9796
4.375 | 12223 | 207.473 | 33.553
4.3854 | 12076 | 214.902 | 36.7102
4.3958 | 15040 | 226.609 | 43.0091
4.4062 | 22202 | 238.297 | 49.2052
4.4167 | 22948 | 255.559 | 54.2938
4.4271 | 23950 | 298.211 | 62.9163
4.4375 | 26314 | 334.153 | 68.8839
4.4479 | 28447 | 368.497 | 74.1426
4.4583 | 30682 | 402.767 | 77.3936
4.4688 | 30926 | 434.341 | 78.5554
4.4792 | 30720 | 463.112 | 76.5077
4.4896 | 30737 | 484.454 | 72.5487
4.5 | 30540 | 502.265 | 71.479
4.5104 | 29790 | 517.266 | 69.8207
4.5208 | 26113 | 527.245 | 66.8543
4.5312 | 24983 | 533.06 | 64.6641
4.5417 | 24349 | 523.24 | 62.3649
4.5521 | 23979 | 514.893 | 60.7385
4.5625 | 23658 | 507.141 | 59.6223
4.5729 | 22068 | 500.749 | 58.2353
4.5833 | 24127 | 495.185 | 57.7369
4.5938 | 23345 | 485.528 | 57.2504
4.6042 | 22595 | 486.089 | 56.6056
4.6146 | 21580 | 481.879 | 56.0848
4.625 | 21228 | 472.845 | 54.3665
4.6354 | 21217 | 460.952 | 53.2605
4.6458 | 20623 | 451.353 | 52.65
4.6562 | 20848 | 444.386 | 52.7577
4.6667 | 20232 | 437.551 | 52.796
4.6771 | 19893 | 433.371 | 52.3779
4.6875 | 19487 | 429.056 | 52.4705
4.6979 | 18819 | 425.985 | 53.2629
4.7083 | 18441 | 418.967 | 52.7517
4.7188 | 18045 | 409.461 | 51.5261
4.7292 | 17864 | 397.339 | 49.6093
4.7396 | 17775 | 388.533 | 48.9427
4.75 | 18608 | 380.723 | 48.6296
4.7604 | 21808 | 376.141 | 49.6914
4.7708 | 20969 | 375.871 | 50.5147
4.7812 | 21559 | 387.657 | 52.3128
4.7917 | 20558 | 390.1 | 53.6433
4.8021 | 19310 | 394.71 | 53.6845
4.8125 | 17043 | 394.839 | 50.9452
4.8229 | 17878 | 395.529 | 52.9297
4.8333 | 21360 | 385.882 | 52.9125
4.8438 | 22636 | 382.453 | 53.4169
4.8542 | 22542 | 394.058 | 56.0453
4.8646 | 24225 | 407.791 | 58.8591
4.875 | 20907 | 416.799 | 59.5274
4.8854 | 18809 | 431.235 | 61.4901
4.8958 | 20576 | 431.369 | 62.2881
4.9062 | 25680 | 424.259 | 62.5216
4.9167 | 23444 | 425.189 | 61.7995
4.9271 | 23139 | 442.605 | 62.9656
4.9375 | 23551 | 446.529 | 63.1246
4.9479 | 20895 | 448.304 | 62.498
4.9583 | 26044 | 450.677 | 62.8879
4.9688 | 24830 | 442.837 | 61.3545
4.9792 | 23966 | 454.13 | 60.2793
4.9896 | 23311 | 458.097 | 59.0631
5 | 22576 | 458.31 | 58.0896
5.0104 | 20411 | 454.219 | 56.9045
5.0208 | 20408 | 449.755 | 56.5323
5.0312 | 18616 | 399.989 | 54.3197
5.0417 | 18359 | 394.865 | 54.6464
5.0521 | 18040 | 391.764 | 56.0247
5.0625 | 17452 | 388.442 | 57.8703
5.0729 | 17034 | 398.901 | 61.3299
5.0833 | 16480 | 388.491 | 60.7043
5.0938 | 15778 | 375.328 | 58.7609
5.1042 | 15863 | 365.261 | 57.7455
5.1146 | 15636 | 353.352 | 54.773
5.125 | 14246 | 341.704 | 54.2506
5.1354 | 13234 | 320.789 | 50.0168
5.1458 | 12513 | 308.975 | 47.1829
5.1562 | 11946 | 292.417 | 43.2167
5.1667 | 11373 | 276.711 | 39.7989
5.1771 | 11968 | 266.792 | 37.922
5.1875 | 11468 | 256.391 | 36.0607
5.1979 | 11771 | 247.469 | 33.6141
5.2083 | 12929 | 246.049 | 33.8758
5.2188 | 12195 | 242.005 | 33.7971
5.2292 | 13090 | 240.775 | 33.8217
5.2396 | 13414 | 241.083 | 33.7925
5.25 | 13404 | 240.418 | 33.687
5.2604 | 12250 | 236.456 | 33.323
5.2708 | 12275 | 233.437 | 33.0618
5.2812 | 11669 | 228.794 | 32.7299
5.2917 | 11895 | 225.718 | 32.3323
5.3021 | 11705 | 222.563 | 32.0183
5.3125 | 11843 | 220.665 | 31.9139
5.3229 | 12189 | 220.054 | 32.0175
5.3333 | 12669 | 220.996 | 32.417
5.3438 | 12645 | 221.556 | 32.8755
5.3542 | 12456 | 221.863 | 33.2595
5.3646 | 13219 | 224.498 | 33.9222
5.375 | 13732 | 229.249 | 34.8031
5.3854 | 16832 | 242.485 | 38.5095
5.3958 | 16830 | 264.33 | 45.1813
5.4062 | 21148 | 298.6 | 52.554
5.4167 | 24560 | 337.077 | 59.1388
5.4271 | 23953 | 375.399 | 67.3838
5.4375 | 25904 | 413.696 | 73.5202
5.4479 | 27488 | 452.36 | 79.0333
5.4583 | 29553 | 486.992 | 82.3513
5.4688 | 29829 | 512.038 | 83.1167
5.4792 | 29837 | 527.074 | 80.2506
5.4896 | 29558 | 534.619 | 75.3918
5.5 | 26139 | 530.642 | 72.4019
5.5104 | 24930 | 523.226 | 69.2958
5.5208 | 24925 | 514.117 | 65.8659
5.5312 | 23924 | 503.532 | 62.7521
5.5417 | 23857 | 496.759 | 60.7403
5.5521 | 21088 | 482.346 | 58.3554
5.5625 | 24802 | 487.172 | 58.6697
5.5729 | 24220 | 488.185 | 57.8984
5.5833 | 22794 | 483.723 | 56.8406
5.5938 | 21983 | 478.182 | 56.5945
5.6042 | 19441 | 463.805 | 54.8111
5.6146 | 17806 | 443.922 | 53.3417
5.625 | 23695 | 451.218 | 53.5368
5.6354 | 21662 | 445.711 | 52.4682
5.6458 | 20152 | 436.331 | 51.7294
5.6562 | 21161 | 433.833 | 52.2112
5.6667 | 17348 | 417.816 | 51.2607
5.6771 | 16651 | 402.052 | 50.1672
5.6875 | 18264 | 397.534 | 50.5418
5.6979 | 18220 | 394.731 | 51.4456
5.7083 | 18613 | 392.367 | 51.3013
5.7188 | 18056 | 386.359 | 50.2523
5.7292 | 17578 | 376.468 | 48.4223
5.7396 | 17335 | 368.187 | 47.7673
5.75 | 17638 | 364.455 | 47.6068
5.7604 | 17744 | 363.648 | 48.4783
5.7708 | 17747 | 363.481 | 49.4192
5.7812 | 17733 | 364.512 | 50.5312
5.7917 | 21738 | 376.541 | 53.0298
5.8021 | 21176 | 383.808 | 53.3209
5.8125 | 20749 | 388.158 | 51.0733
5.8229 | 21158 | 398.101 | 53.517
5.8333 | 17930 | 391.676 | 52.7868
5.8438 | 19535 | 394.139 | 53.6733
5.8542 | 22636 | 409.78 | 56.9581
5.8646 | 21182 | 417.213 | 58.9787
5.875 | 21436 | 423.276 | 59.968
5.8854 | 20522 | 426.09 | 61.4483
5.8958 | 18098 | 420.05 | 61.307
5.9062 | 24479 | 439.141 | 63.2192
5.9167 | 22590 | 445.192 | 62.8253
5.9271 | 21673 | 445.769 | 62.9284
5.9375 | 21063 | 443.699 | 62.5903
5.9479 | 16683 | 424.981 | 60.5834
5.9583 | 24122 | 438.815 | 61.9038
5.9688 | 21831 | 438.995 | 60.6811
5.9792 | 22589 | 440.223 | 59.2644
5.9896 | 21074 | 435.94 | 57.4484
6 | 18895 | 424.663 | 55.6212
6.0104 | 16990 | 338.279 | 50.0026
6.0208 | 16990 | 331.66 | 49.5169
6.0312 | 15964 | 328.748 | 50.0852
6.0417 | 15806 | 334.966 | 51.0516
6.0521 | 15610 | 338.529 | 52.819
6.0625 | 15247 | 345.206 | 55.2486
6.0729 | 14989 | 351.794 | 58.5205
6.0833 | 14647 | 338.589 | 57.7894
6.0938 | 14212 | 326.681 | 55.9646
6.1042 | 14266 | 317.322 | 54.9879
6.1146 | 14126 | 305.764 | 52.0524
6.125 | 13264 | 298.654 | 51.8564
6.1354 | 12636 | 283.361 | 47.9766
6.1458 | 12189 | 276.608 | 45.4481
6.1562 | 11836 | 264.125 | 41.7228
6.1667 | 11481 | 253.269 | 38.5838
6.1771 | 11851 | 244.348 | 36.736
6.1875 | 11540 | 235.974 | 34.9997
6.1979 | 11729 | 229.963 | 32.694
6.2083 | 12450 | 225.821 | 32.7715
6.2188 | 11994 | 223.206 | 32.7946
6.2292 | 12552 | 220.635 | 32.7174
6.2396 | 12755 | 219.725 | 32.6135
6.25 | 12749 | 217.828 | 32.4437
6.2604 | 12030 | 217.397 | 32.3053
6.2708 | 12046 | 217.63 | 32.2152
6.2812 | 11668 | 215.643 | 32.0419
6.2917 | 11810 | 214.125 | 31.7186
6.3021 | 11692 | 213.966 | 31.5665
6.3125 | 11778 | 214.649 | 31.5945
6.3229 | 11994 | 213.705 | 31.6718
6.3333 | 12294 | 213.435 | 31.9941
6.3438 | 12280 | 213.269 | 32.4142
6.3542 | 12162 | 213.185 | 32.7838
6.3646 | 12640 | 215.238 | 33.394
6.375 | 12962 | 217.104 | 34.1071
6.3854 | 14903 | 221.997 | 37.2643
6.3958 | 14903 | 238.126 | 43.6203
6.4062 | 17608 | 265.681 | 50.4294
6.4167 | 19748 | 288.665 | 55.9379
6.4271 | 19370 | 317.918 | 63.6591
6.4375 | 20596 | 345.785 | 69.0288
6.4479 | 21592 | 374.034 | 73.7682
6.4583 | 22891 | 399.399 | 76.3136
6.4688 | 23068 | 416.261 | 76.5079
6.4792 | 23077 | 424.12 | 73.1623
6.4896 | 22905 | 426.867 | 68.0025
6.5 | 20762 | 429.12 | 65.6899
6.5104 | 20005 | 429.274 | 63.1283
6.5208 | 20005 | 419.678 | 59.6768
6.5312 | 19379 | 410.599 | 56.7522
6.5417 | 19339 | 401.486 | 54.6182
6.5521 | 17601 | 395.896 | 52.9966
6.5625 | 19939 | 391.3 | 52.4411
6.5729 | 19576 | 384.906 | 51.3064
6.5833 | 18681 | 385.221 | 50.6582
6.5938 | 18173 | 384.074 | 50.7412
6.6042 | 16574 | 381.34 | 49.8416
6.6146 | 15545 | 376.127 | 49.3228
6.625 | 19259 | 368.552 | 48.2172
6.6354 | 17980 | 361.503 | 47.2342
6.6458 | 17030 | 355.44 | 46.8131
6.6562 | 17669 | 351.76 | 47.1508
6.6667 | 15264 | 348.452 | 47.2093
6.6771 | 14826 | 345.533 | 46.873
6.6875 | 15846 | 343.854 | 47.299
6.6979 | 15819 | 342.747 | 48.3049
6.7083 | 16069 | 338.081 | 48.0123
6.7188 | 15719 | 332.083 | 47.0043
6.7292 | 15418 | 323.696 | 45.2919
6.7396 | 15266 | 319.073 | 44.8557
6.75 | 15459 | 316.907 | 44.7646
6.7604 | 15528 | 323.517 | 46.0334
6.7708 | 15531 | 327.252 | 47.1876
6.7812 | 15524 | 332.832 | 48.5483
6.7917 | 18062 | 332.175 | 50.1097
6.8021 | 17708 | 329.891 | 49.8971
6.8125 | 17440 | 323.65 | 47.0883
6.8229 | 17701 | 325.33 | 49.0408
6.8333 | 15656 | 330.898 | 49.1948
6.8438 | 16676 | 338.019 | 50.2296
6.8542 | 18646 | 345.666 | 52.8482
6.8646 | 17726 | 356.327 | 55.141
6.875 | 17889 | 356.764 | 55.7966
6.8854 | 17311 | 354.572 | 57.066
6.8958 | 15773 | 357.441 | 57.5921
6.9062 | 19830 | 369.355 | 58.6288
6.9167 | 18631 | 372.87 | 58.2234
6.9271 | 18051 | 374.18 | 58.434
6.9375 | 17665 | 375.615 | 58.3352
6.9479 | 14880 | 370.46 | 57.3949
6.9583 | 19617 | 376.895 | 57.7698
6.9688 | 18161 | 378.534 | 56.7891
6.9792 | 18646 | 376.09 | 55.1058
6.9896 | 17683 | 373.579 | 53.5013
7 | 16297 | 370.197 | 52.2749
7.0104 | 15388 | 360.726 | 51.0389
7.0208 | 15534 | 354.752 | 50.6085
7.0312 | 15779 | 328.749 | 50.0655
7.0417 | 18281 | 334.966 | 51.322
7.0521 | 17472 | 338.529 | 53.0234
7.0625 | 18215 | 345.206 | 55.579
7.0729 | 18130 | 351.794 | 58.8735
7.0833 | 13548 | 338.589 | 57.6727
7.0938 | 13661 | 326.681 | 55.9083
7.1042 | 13676 | 317.322 | 54.9294
7.1146 | 13339 | 305.764 | 51.977
7.125 | 13075 | 298.653 | 51.8388
7.1354 | 12042 | 283.361 | 47.9233
7.1458 | 12042 | 276.608 | 45.4355
7.1562 | 11397 | 264.124 | 41.6864
7.1667 | 11220 | 253.269 | 38.563
7.1771 | 10898 | 244.347 | 36.663
7.1875 | 10627 | 235.973 | 34.9325
7.1979 | 11347 | 229.963 | 32.6665
7.2083 | 10876 | 225.821 | 32.6614
7.2188 | 11186 | 223.206 | 32.7391
7.2292 | 11343 | 220.635 | 32.6356
7.2396 | 11624 | 219.725 | 32.5377
7.25 | 11522 | 217.828 | 32.3623
7.2604 | 11844 | 217.398 | 32.2931
7.2708 | 12105 | 217.63 | 32.2191
7.2812 | 11429 | 215.643 | 32.0262
7.2917 | 11457 | 214.125 | 31.6958
7.3021 | 11826 | 213.966 | 31.5752
7.3125 | 12021 | 214.649 | 31.6103
7.3229 | 11488 | 213.704 | 31.6392
7.3333 | 11613 | 213.435 | 31.9504
7.3438 | 11632 | 213.269 | 32.3728
7.3542 | 11482 | 213.184 | 32.7405
7.3646 | 12270 | 215.239 | 33.3703
7.375 | 11978 | 217.105 | 34.0437
7.3854 | 11889 | 221.997 | 37.07
7.3958 | 13692 | 238.127 | 43.5396
7.4062 | 18050 | 265.682 | 50.4621
7.4167 | 18506 | 288.665 | 55.8381
7.4271 | 19118 | 317.918 | 63.6372
7.4375 | 20560 | 345.785 | 69.0254
7.4479 | 21862 | 374.034 | 73.796
7.4583 | 23227 | 399.399 | 76.3514
7.4688 | 23379 | 416.261 | 76.5453
7.4792 | 23258 | 424.12 | 73.1852
7.4896 | 23272 | 426.868 | 68.0511
7.5 | 23155 | 429.121 | 66.0177
7.5104 | 22701 | 429.274 | 63.5055
7.5208 | 20461 | 419.677 | 59.74
7.5312 | 19774 | 410.6 | 56.8065
7.5417 | 19390 | 401.486 | 54.6251
7.5521 | 19166 | 395.896 | 53.2063
7.5625 | 18973 | 391.3 | 52.3131
7.5729 | 18003 | 384.906 | 51.1024
7.5833 | 19264 | 385.221 | 50.7339
7.5938 | 18789 | 384.074 | 50.8204
7.6042 | 18332 | 381.34 | 50.0653
7.6146 | 17713 | 376.127 | 49.5938
7.625 | 17500 | 368.552 | 48.0008
7.6354 | 17495 | 361.503 | 47.1754
7.6458 | 17134 | 355.44 | 46.8255
7.6562 | 17273 | 351.76 | 47.1041
7.6667 | 16898 | 348.452 | 47.3997
7.6771 | 16692 | 345.533 | 47.0874
7.6875 | 16445 | 343.854 | 47.3668
7.6979 | 16037 | 342.747 | 48.3291
7.7083 | 15806 | 338.081 | 47.9836
7.7188 | 15565 | 332.082 | 46.9879
7.7292 | 15456 | 323.697 | 45.2959
7.7396 | 15402 | 319.073 | 44.8699
7.75 | 15915 | 316.907 | 44.8118
7.7604 | 17883 | 323.517 | 46.2824
7.7708 | 17370 | 327.252 | 47.3835
7.7812 | 17735 | 332.832 | 48.7867
7.7917 | 17121 | 332.174 | 50.0082
7.8021 | 16355 | 329.89 | 49.7523
7.8125 | 14962 | 323.651 | 46.8301
7.8229 | 15477 | 325.331 | 48.8117
7.8333 | 17623 | 330.898 | 49.4017
7.8438 | 18411 | 338.02 | 50.4167
7.8542 | 18356 | 345.666 | 52.8164
7.8646 | 19395 | 356.327 | 55.3293
7.875 | 17352 | 356.764 | 55.7363
7.8854 | 16060 | 354.572 | 56.9284
7.8958 | 17152 | 357.44 | 57.744
7.9062 | 20304 | 369.356 | 58.6834
7.9167 | 18926 | 372.87 | 58.2577
7.9271 | 18740 | 374.18 | 58.5149
7.9375 | 18997 | 375.615 | 58.4932
7.9479 | 17359 | 370.46 | 57.6853
7.9583 | 20544 | 376.896 | 57.8821
7.9688 | 19796 | 378.534 | 56.9899
7.9792 | 19265 | 376.091 | 55.1821
7.9896 | 18862 | 373.58 | 53.6467
8 | 18409 | 370.196 | 52.5341
8.0104 | 21477 | 407.888 | 54.4476
8.0208 | 21474 | 405.876 | 54.2133
8.0312 | 19620 | 399.989 | 54.459
8.0417 | 19334 | 394.865 | 54.7792
8.0521 | 18978 | 391.764 | 56.1501
8.0625 | 18321 | 388.441 | 57.984
8.0729 | 17855 | 398.902 | 61.4396
8.0833 | 17237 | 388.491 | 60.8017
8.0938 | 16453 | 375.328 | 58.8446
8.1042 | 16548 | 365.261 | 57.828
8.1146 | 16295 | 353.352 | 54.8502
8.125 | 14743 | 341.929 | 54.3289
8.1354 | 13613 | 320.789 | 50.0572
8.1458 | 12807 | 308.975 | 47.2126
8.1562 | 12173 | 292.417 | 43.2385
8.1667 | 11533 | 276.711 | 39.8134
8.1771 | 12198 | 266.791 | 37.9419
8.1875 | 11640 | 256.39 | 36.0749
8.1979 | 11978 | 247.469 | 33.6307
8.2083 | 13272 | 246.049 | 33.9029
8.2188 | 12452 | 242.006 | 33.817
8.2292 | 13453 | 240.775 | 33.8495
8.2396 | 13815 | 241.083 | 33.8232
8.25 | 13803 | 240.417 | 33.7176
8.2604 | 12514 | 236.456 | 33.3428
8.2708 | 12542 | 233.436 | 33.0814
8.2812 | 11865 | 228.794 | 32.7439
8.2917 | 12118 | 225.718 | 32.3479
8.3021 | 11906 | 222.562 | 32.032
8.3125 | 12059 | 220.665 | 31.9285
8.3229 | 12446 | 220.054 | 32.0348
8.3333 | 12982 | 220.996 | 32.4383
8.3438 | 12956 | 221.556 | 32.8965
8.3542 | 12745 | 221.863 | 33.279
8.3646 | 13597 | 224.497 | 33.9482
8.375 | 14171 | 229.249 | 34.8338
8.3854 | 17637 | 242.485 | 38.5688
8.3958 | 17635 | 264.33 | 45.2445
8.4062 | 22461 | 298.601 | 52.6706
8.4167 | 26276 | 337.077 | 59.3141
8.4271 | 25598 | 375.399 | 67.5693
8.4375 | 27780 | 413.696 | 73.7548
8.4479 | 29551 | 452.36 | 79.3185
8.4583 | 31861 | 486.992 | 82.7013
8.4688 | 32171 | 512.038 | 83.4993
8.4792 | 32180 | 527.073 | 80.6565
8.4896 | 31869 | 534.619 | 75.81
8.5 | 28047 | 530.642 | 72.7503
8.5104 | 26695 | 523.226 | 69.6174
8.5208 | 26690 | 514.116 | 66.1859
8.5312 | 25572 | 503.532 | 63.0469
8.5417 | 25496 | 496.76 | 61.0328
8.5521 | 22401 | 482.346 | 58.5822
8.5625 | 26555 | 487.172 | 58.9774
8.5729 | 25905 | 488.184 | 58.195
8.5833 | 24310 | 483.723 | 57.1044
8.5938 | 23404 | 478.181 | 56.8374
8.6042 | 20560 | 463.806 | 54.995
8.6146 | 18732 | 443.922 | 53.4856
8.625 | 25320 | 451.218 | 53.7971
8.6354 | 23046 | 445.711 | 52.6887
8.6458 | 21357 | 436.331 | 51.9174
8.6562 | 22487 | 433.833 | 52.4168
8.6667 | 18221 | 417.816 | 51.3897
8.6771 | 17442 | 402.053 | 50.2781
8.6875 | 19246 | 397.534 | 50.6766
8.6979 | 19197 | 394.731 | 51.5771
8.7083 | 19637 | 392.367 | 51.4381
8.7188 | 19014 | 386.358 | 50.3783
8.7292 | 18480 | 376.467 | 48.5387
8.7396 | 18208 | 368.187 | 47.8773
8.75 | 18547 | 364.455 | 47.7202
8.7604 | 18666 | 363.648 | 48.5924
8.7708 | 18670 | 363.481 | 49.5326
8.7812 | 18654 | 364.512 | 50.6437
8.7917 | 23137 | 376.541 | 53.2088
8.8021 | 22509 | 383.808 | 53.4958
8.8125 | 22031 | 388.158 | 51.2442
8.8229 | 22489 | 398.101 | 53.6977
8.8333 | 18876 | 391.676 | 52.9122
8.8438 | 20674 | 394.139 | 53.8248
8.8542 | 24145 | 409.78 | 57.1672
8.8646 | 22518 | 417.213 | 59.166
8.875 | 22803 | 423.276 | 60.1623
8.8854 | 21780 | 426.09 | 61.6272
8.8958 | 19067 | 420.05 | 61.441
8.9062 | 26211 | 439.142 | 63.4727
8.9167 | 24096 | 445.193 | 63.0497
8.9271 | 23071 | 445.77 | 63.1375
8.9375 | 22388 | 443.7 | 62.7881
8.9479 | 17483 | 424.981 | 60.6968
8.9583 | 25814 | 438.815 | 62.1559
8.9688 | 23248 | 438.995 | 60.8938
8.9792 | 24098 | 440.224 | 59.4942
8.9896 | 22402 | 435.94 | 57.6494
9 | 19962 | 424.663 | 55.7783
9.0104 | 18363 | 408.694 | 54.0516
9.0208 | 18618 | 398.5 | 53.4007
9.0312 | 19046 | 393.304 | 54.0075
9.0417 | 23433 | 403.839 | 55.8545
9.0521 | 22011 | 408.218 | 57.4939
9.0625 | 23310 | 417.413 | 60.3045
9.0729 | 23158 | 425.681 | 63.6883
9.0833 | 15122 | 402.222 | 61.2693
9.0938 | 15319 | 383.34 | 59.1363
9.1042 | 15342 | 368.602 | 57.8635
9.1146 | 14751 | 351.82 | 54.5865
9.125 | 14287 | 339.78 | 54.1525
9.1354 | 12478 | 319.354 | 49.8604
9.1458 | 12477 | 306.971 | 47.074
9.1562 | 11347 | 288.387 | 42.9496
9.1667 | 11037 | 272.158 | 39.5317
9.1771 | 10473 | 258.031 | 37.3391
9.1875 | 10000 | 244.708 | 35.3368
9.1979 | 11258 | 236.118 | 32.9808
9.2083 | 10436 | 228.58 | 32.7737
9.2188 | 10976 | 223.715 | 32.7521
9.2292 | 11250 | 219.452 | 32.5682
9.2396 | 11740 | 217.583 | 32.4339
9.25 | 11562 | 214.543 | 32.1927
9.2604 | 12124 | 213.759 | 32.1201
9.2708 | 12578 | 214.146 | 32.0666
9.2812 | 11399 | 210.837 | 31.773
9.2917 | 11448 | 208.333 | 31.3923
9.3021 | 12090 | 208.104 | 31.2846
9.3125 | 12429 | 209.075 | 31.3436
9.3229 | 11500 | 207.25 | 31.3023
9.3333 | 11717 | 206.549 | 31.5964
9.3438 | 11751 | 206.058 | 32.0027
9.3542 | 11489 | 205.392 | 32.3337
9.3646 | 12859 | 208.553 | 33.0549
9.375 | 12350 | 210.671 | 33.7288
9.3854 | 20185 | 142.131 | 22.2036
9.3958 | 28020 | 142.394 | 23.7998
9.4062 | 35855 | 186.352 | 32.7934
9.4167 | 43690 | 180.967 | 31.1213
9.4271 | 44749 | 206.005 | 36.4424
9.4375 | 47249 | 236.808 | 41.638
9.4479 | 49504 | 268.795 | 46.4885
9.4583 | 51868 | 301.026 | 50.2141
9.4688 | 52126 | 320.341 | 51.0423
9.4792 | 51909 | 331.025 | 49.2731
9.4896 | 51927 | 338.339 | 46.4993
9.5 | 51719 | 343.351 | 45.416
9.5104 | 50926 | 343.251 | 43.5825
9.5208 | 47039 | 319.893 | 38.7693
9.5312 | 45844 | 307.669 | 36.1991
9.5417 | 45174 | 297.844 | 34.4309
9.5521 | 44783 | 291.435 | 33.294
9.5625 | 44444 | 285.906 | 32.4927
9.5729 | 42762 | 271.846 | 30.5653
9.5833 | 44940 | 282.28 | 31.7799
9.5938 | 44113 | 276.961 | 31.2493
9.6042 | 43320 | 270.38 | 30.2439
9.6146 | 42247 | 260.519 | 29.1698
9.625 | 41875 | 253.002 | 27.9837
9.6354 | 41863 | 247.889 | 27.4627
9.6458 | 41236 | 240.138 | 26.7768
9.6562 | 41473 | 238.255 | 27.0103
9.6667 | 40822 | 232.055 | 26.648
9.6771 | 40463 | 227.455 | 26.1651
9.6875 | 40034 | 223.106 | 25.9293
9.6979 | 39328 | 217.455 | 25.8146
9.7083 | 38928 | 211.613 | 25.2661
9.7188 | 38510 | 205.098 | 24.394
9.7292 | 38319 | 198.767 | 23.368
9.7396 | 38224 | 194.905 | 23.03
9.75 | 39106 | 197.495 | 23.5766
9.7604 | 42491 | 216.947 | 26.5625
9.7708 | 41604 | 216.052 | 26.6399
9.7812 | 42228 | 222.571 | 27.8292
9.7917 | 41169 | 217.833 | 27.7764
9.8021 | 39849 | 210.029 | 26.6857
9.8125 | 37451 | 193.461 | 23.4057
9.8229 | 38335 | 197.63 | 24.9463
9.8333 | 42018 | 218.356 | 27.8782
9.8438 | 43369 | 229.755 | 29.4008
9.8542 | 43270 | 235.082 | 30.727
9.8646 | 45050 | 250.698 | 33.4109
9.875 | 41540 | 235.503 | 31.1931
9.8854 | 39321 | 221.932 | 29.9594
9.8958 | 41190 | 232.524 | 31.8646
9.9062 | 46591 | 265.813 | 36.3932
9.9167 | 44225 | 259.443 | 34.6638
9.9271 | 43902 | 259.567 | 34.6275
9.9375 | 44339 | 263.317 | 34.9873
9.9479 | 41529 | 246.421 | 32.4252
9.9583 | 46978 | 277.014 | 36.5187
9.9688 | 45693 | 274.258 | 35.2843
9.9792 | 44779 | 269.503 | 33.7072
9.9896 | 44086 | 265.021 | 32.4026
10 | 43308 | 259.114 | 31.2472
10.0104 | 41017 | 241.208 | 28.8598
10.0208 | 41014 | 236.643 | 28.5387
10.0312 | 39118 | 213.699 | 26.7416
10.0417 | 38847 | 212.549 | 26.8516
10.0521 | 38509 | 209.158 | 27.2505
10.0625 | 37886 | 204.895 | 27.6599
10.0729 | 37445 | 202.023 | 28.6069
10.0833 | 36858 | 196.018 | 27.8989
10.0938 | 36116 | 193.514 | 26.7511
10.1042 | 36206 | 188.2 | 26.308
10.1146 | 35965 | 180.184 | 24.6919
10.125 | 34494 | 168.633 | 23.2177
10.1354 | 33423 | 156.181 | 20.5944
10.1458 | 32660 | 147.781 | 18.8042
10.1562 | 32059 | 137.977 | 16.7467
10.1667 | 31453 | 128.618 | 14.9536
10.1771 | 32083 | 126.664 | 14.679
10.1875 | 31554 | 118.941 | 13.5231
10.1979 | 31875 | 116.581 | 12.8176
10.2083 | 33101 | 118.725 | 13.5832
10.2188 | 32323 | 113.196 | 13.0136
10.2292 | 33271 | 116.198 | 13.6089
10.2396 | 33614 | 115.88 | 13.7132
10.25 | 33604 | 115.321 | 13.6512
10.2604 | 32382 | 110.579 | 12.8318
10.2708 | 32408 | 110.577 | 12.8037
10.2812 | 31767 | 106.396 | 12.2708
10.2917 | 32006 | 106.154 | 12.2749
10.3021 | 31805 | 103.683 | 12.0022
10.3125 | 31951 | 103.286 | 12.0432
10.3229 | 32317 | 103.591 | 12.267
10.3333 | 32825 | 104.706 | 12.6741
10.3438 | 32800 | 104.391 | 12.8144
10.3542 | 32600 | 104.192 | 12.8608
10.3646 | 33408 | 107.381 | 13.5834
10.375 | 33952 | 109.695 | 14.1918
10.3854 | 37235 | 122.962 | 17.5429
10.3958 | 37233 | 129.593 | 20.4402
10.4062 | 41804 | 152.652 | 26.4489
10.4167 | 45418 | 172.388 | 31.4213
10.4271 | 44776 | 191.576 | 35.6163
10.4375 | 46842 | 220.702 | 40.4711
10.4479 | 48519 | 244.921 | 44.5411
10.4583 | 50707 | 270.93 | 47.7947
10.4688 | 51000 | 288.955 | 48.5596
10.4792 | 51009 | 302.94 | 47.1239
10.4896 | 50713 | 311.856 | 44.3385
10.5 | 47093 | 305.938 | 41.037
10.5104 | 45812 | 306.305 | 39.0402
10.5208 | 45808 | 304.355 | 37.2929
10.5312 | 44748 | 295.725 | 35.0103
10.5417 | 44677 | 291.288 | 33.8322
10.5521 | 41745 | 272.682 | 30.8576
10.5625 | 45678 | 290.431 | 33.2688
10.5729 | 45062 | 280.662 | 32.0408
10.5833 | 43552 | 277.177 | 30.9147
10.5938 | 42693 | 274.171 | 30.4877
10.6042 | 40001 | 257.618 | 28.0529
10.6146 | 38269 | 243.997 | 26.4057
10.625 | 44508 | 266.844 | 29.8364
10.6354 | 42354 | 244.881 | 27.4913
10.6458 | 40755 | 241.694 | 26.6608
10.6562 | 41824 | 245.448 | 27.5664
10.6667 | 37785 | 221.024 | 24.6254
10.6771 | 37047 | 216.351 | 23.9396
10.6875 | 38755 | 219.096 | 25.1157
10.6979 | 38708 | 212.502 | 25.2419
10.7083 | 39125 | 211.171 | 25.3356
10.7188 | 38535 | 204.492 | 24.3722
10.7292 | 38029 | 198.871 | 23.2387
10.7396 | 37772 | 194.964 | 22.8223
10.75 | 38093 | 193.473 | 22.8935
10.7604 | 38205 | 191.276 | 23.2538
10.7708 | 38209 | 190.843 | 23.6843
10.7812 | 38193 | 191.066 | 24.1923
10.7917 | 42437 | 207.281 | 27.7453
10.8021 | 41842 | 204.039 | 27.2735
10.8125 | 41390 | 208.862 | 26.0852
10.8229 | 41824 | 216.762 | 27.6701
10.8333 | 38403 | 204.067 | 25.3674
10.8438 | 40104 | 215.513 | 27.1111
10.8542 | 43390 | 227.452 | 30.3415
10.8646 | 41850 | 223.816 | 30.3667
10.875 | 42120 | 232.313 | 31.3034
10.8854 | 41151 | 231.253 | 31.4972
10.8958 | 38582 | 221.848 | 29.7807
10.9062 | 45345 | 253.43 | 35.0987
10.9167 | 43343 | 240.885 | 33.1626
10.9271 | 42372 | 245.724 | 33.0639
10.9375 | 41725 | 244.964 | 32.6154
10.9479 | 37083 | 219.991 | 28.3753
10.9583 | 44968 | 257.285 | 34.4586
10.9688 | 42540 | 236.835 | 31.6432
10.9792 | 43343 | 246.946 | 31.7502
10.9896 | 41738 | 239.743 | 29.8773
11 | 39429 | 229.93 | 27.7516
11.0104 | 37915 | 219.004 | 26.0654
11.0208 | 38156 | 214.972 | 25.9114
11.0312 | 38561 | 211.31 | 26.3209
11.0417 | 42713 | 226.16 | 29.4966
11.0521 | 41366 | 219.077 | 29.2933
11.0625 | 42596 | 231.276 | 31.6924
11.0729 | 42452 | 233.98 | 33.3265
11.0833 | 34847 | 196.987 | 26.5404
11.0938 | 35033 | 198.724 | 26.2813
11.1042 | 35055 | 187.683 | 25.4959
11.1146 | 34496 | 175.536 | 23.4785
11.125 | 34056 | 167.55 | 22.8577
11.1354 | 32345 | 149.33 | 19.4929
11.1458 | 32344 | 145.229 | 18.462
11.1562 | 31274 | 132.964 | 15.9924
11.1667 | 30981 | 125.284 | 14.502
11.1771 | 30448 | 116.69 | 13.2492
11.1875 | 30000 | 109.449 | 12.1856
11.1979 | 31190 | 110.237 | 12.1585
11.2083 | 30412 | 102.751 | 11.4667
11.2188 | 30923 | 103.076 | 11.8093
11.2292 | 31182 | 101.234 | 11.8491
11.2396 | 31646 | 101.306 | 12.0526
11.25 | 31478 | 99.0778 | 11.8303
11.2604 | 32009 | 100.25 | 12.1169
11.2708 | 32439 | 100.785 | 12.3019
11.2812 | 31323 | 96.3554 | 11.5352
11.2917 | 31370 | 96.5936 | 11.4785
11.3021 | 31977 | 97.6322 | 11.7636
11.3125 | 32298 | 97.9874 | 11.9209
11.3229 | 31419 | 94.9242 | 11.4011
11.3333 | 31624 | 96.0237 | 11.6707
11.3438 | 31656 | 95.4783 | 11.8159
11.3542 | 31409 | 94.4815 | 11.7835
11.3646 | 32704 | 98.8791 | 12.8111
11.375 | 32223 | 97.3202 | 12.7275
11.3854 | 32076 | 99.6122 | 13.8207
11.3958 | 30044.5 | 128.421 | 21.53
11.4062 | 28013 | 195.088 | 38.9981
11.4167 | 27446.7 | 218.588 | 45.3947
11.4271 | 26880.3 | 268.972 | 56.0576
11.4375 | 26314 | 334.153 | 68.8839
11.4479 | 28447 | 368.497 | 74.1426
11.4583 | 30682 | 402.767 | 77.3936
11.4688 | 30926 | 434.341 | 78.5554
11.4792 | 30720 | 463.112 | 76.5077
11.4896 | 30737 | 484.454 | 72.5487
11.5 | 30540 | 502.265 | 71.479
11.5104 | 29790 | 517.266 | 69.8207
11.5208 | 26113 | 527.245 | 66.8543
11.5312 | 24983 | 533.06 | 64.6641
11.5417 | 24349 | 523.24 | 62.3649
11.5521 | 23979 | 514.893 | 60.7385
11.5625 | 23658 | 507.141 | 59.6223
11.5729 | 22068 | 500.749 | 58.2353
11.5833 | 24127 | 495.185 | 57.7369
11.5938 | 23345 | 485.528 | 57.2504
11.6042 | 22595 | 486.089 | 56.6056
11.6146 | 21580 | 481.879 | 56.0848
11.625 | 21228 | 472.845 | 54.3665
11.6354 | 21217 | 460.952 | 53.2605
11.6458 | 20623 | 451.353 | 52.65
11.6562 | 20848 | 444.386 | 52.7577
11.6667 | 20232 | 437.551 | 52.796
11.6771 | 19893 | 433.371 | 52.3779
11.6875 | 19487 | 429.056 | 52.4705
11.6979 | 18819 | 425.985 | 53.2629
11.7083 | 18441 | 418.967 | 52.7517
11.7188 | 18045 | 409.461 | 51.5261
11.7292 | 17864 | 397.339 | 49.6093
11.7396 | 17775 | 388.533 | 48.9427
11.75 | 18608 | 380.723 | 48.6296
11.7604 | 21808 | 376.141 | 49.6914
11.7708 | 20969 | 375.871 | 50.5147
11.7812 | 21559 | 387.657 | 52.3128
11.7917 | 20558 | 390.1 | 53.6433
11.8021 | 19310 | 394.71 | 53.6845
11.8125 | 17043 | 394.839 | 50.9452
11.8229 | 17878 | 395.529 | 52.9297
11.8333 | 21360 | 385.882 | 52.9125
11.8438 | 22636 | 382.453 | 53.4169
11.8542 | 22542 | 394.058 | 56.0453
11.8646 | 24225 | 407.791 | 58.8591
11.875 | 20907 | 416.799 | 59.5274
11.8854 | 18809 | 431.235 | 61.4901
11.8958 | 20576 | 431.369 | 62.2881
11.9062 | 25680 | 424.259 | 62.5216
11.9167 | 23444 | 425.189 | 61.7995
11.9271 | 23139 | 442.605 | 62.9656
11.9375 | 23551 | 446.529 | 63.1246
11.9479 | 20895 | 448.304 | 62.498
11.9583 | 26044 | 450.677 | 62.8879
11.9688 | 24830 | 442.837 | 61.3545
11.9792 | 23966 | 454.13 | 60.2793
11.9896 | 23311 | 458.097 | 59.0631
12 | 22576 | 458.31 | 58.0896
12.0104 | 20411 | 454.219 | 56.9045
12.0208 | 20408 | 449.755 | 56.5323
12.0312 | 18616 | 399.989 | 54.3197
12.0417 | 18359 | 394.865 | 54.6464
12.0521 | 18040 | 391.764 | 56.0247
12.0625 | 17452 | 388.442 | 57.8703
12.0729 | 17034 | 398.901 | 61.3299
12.0833 | 16480 | 388.491 | 60.7043
12.0938 | 15778 | 375.328 | 58.7609
12.1042 | 15863 | 365.261 | 57.7455
12.1146 | 15636 | 353.352 | 54.773
12.125 | 14246 | 341.704 | 54.2506
12.1354 | 13234 | 320.789 | 50.0168
12.1458 | 12513 | 308.975 | 47.1829
12.1562 | 11946 | 292.417 | 43.2167
12.1667 | 11373 | 276.711 | 39.7989
12.1771 | 11968 | 266.792 | 37.922
12.1875 | 11468 | 256.391 | 36.0607
12.1979 | 11771 | 247.469 | 33.6141
12.2083 | 12929 | 246.049 | 33.8758
12.2188 | 12195 | 242.005 | 33.7971
12.2292 | 13090 | 240.775 | 33.8217
12.2396 | 13414 | 241.083 | 33.7925
12.25 | 13404 | 240.418 | 33.687
12.2604 | 12250 | 236.456 | 33.323
12.2708 | 12275 | 233.437 | 33.0618
12.2812 | 11669 | 228.794 | 32.7299
12.2917 | 11895 | 225.718 | 32.3323
12.3021 | 11705 | 222.563 | 32.0183
12.3125 | 11843 | 220.665 | 31.9139
12.3229 | 12189 | 220.054 | 32.0175
12.3333 | 12669 | 220.996 | 32.417
12.3438 | 12645 | 221.556 | 32.8755
12.3542 | 12456 | 221.863 | 33.2595
12.3646 | 13219 | 224.498 | 33.9222
12.375 | 13732 | 229.249 | 34.8031
12.3854 | 16832 | 242.485 | 38.5095
12.3958 | 16830 | 264.33 | 45.1813
12.4062 | 21148 | 298.6 | 52.554
12.4167 | 24560 | 337.077 | 59.1388
12.4271 | 23953 | 375.399 | 67.3838
12.4375 | 25904 | 413.696 | 73.5202
12.4479 | 27488 | 452.36 | 79.0333
12.4583 | 29553 | 486.992 | 82.3513
12.4688 | 29829 | 512.038 | 83.1167
12.4792 | 29837 | 527.074 | 80.2506
12.4896 | 29558 | 534.619 | 75.3918
12.5 | 26139 | 530.642 | 72.4019
12.5104 | 24930 | 523.226 | 69.2958
12.5208 | 24925 | 514.117 | 65.8659
12.5312 | 23924 | 503.532 | 62.7521
12.5417 | 23857 | 496.759 | 60.7403
12.5521 | 21088 | 482.346 | 58.3554
12.5625 | 24802 | 487.172 | 58.6697
12.5729 | 24220 | 488.185 | 57.8984
12.5833 | 22794 | 483.723 | 56.8406
12.5938 | 21983 | 478.182 | 56.5945
12.6042 | 19441 | 463.805 | 54.8111
12.6146 | 17806 | 443.922 | 53.3417
12.625 | 23695 | 451.218 | 53.5368
12.6354 | 21662 | 445.711 | 52.4682
12.6458 | 20152 | 436.331 | 51.7294
12.6562 | 21161 | 433.833 | 52.2112
12.6667 | 17348 | 417.816 | 51.2607
12.6771 | 16651 | 402.052 | 50.1672
12.6875 | 18264 | 397.534 | 50.5418
12.6979 | 18220 | 394.731 | 51.4456
12.7083 | 18613 | 392.367 | 51.3013
12.7188 | 18056 | 386.359 | 50.2523
12.7292 | 17578 | 376.468 | 48.4223
12.7396 | 17335 | 368.187 | 47.7673
12.75 | 17638 | 364.455 | 47.6068
12.7604 | 17744 | 363.648 | 48.4783
12.7708 | 17747 | 363.481 | 49.4192
12.7812 | 17733 | 364.512 | 50.5312
12.7917 | 21738 | 376.541 | 53.0298
12.8021 | 21176 | 383.808 | 53.3209
12.8125 | 20749 | 388.158 | 51.0733
12.8229 | 21158 | 398.101 | 53.517
12.8333 | 17930 | 391.676 | 52.7868
12.8438 | 19535 | 394.139 | 53.6733
12.8542 | 22636 | 409.78 | 56.9581
12.8646 | 21182 | 417.213 | 58.9787
12.875 | 21436 | 423.276 | 59.968
12.8854 | 20522 | 426.09 | 61.4483
12.8958 | 18098 | 420.05 | 61.307
12.9062 | 24479 | 439.141 | 63.2192
12.9167 | 22590 | 445.192 | 62.8253
12.9271 | 21673 | 445.769 | 62.9284
12.9375 | 21063 | 443.699 | 62.5903
12.9479 | 16683 | 424.981 | 60.5834
12.9583 | 24122 | 438.815 | 61.9038
12.9688 | 21831 | 438.995 | 60.6811
12.9792 | 22589 | 440.223 | 59.2644
12.9896 | 21074 | 435.94 | 57.4484
13 | 18895 | 424.663 | 55.6212
13.0104 | 16990 | 338.279 | 50.0026
13.0208 | 16990 | 331.66 | 49.5169
13.0312 | 15964 | 328.748 | 50.0852
13.0417 | 15806 | 334.966 | 51.0516
13.0521 | 15610 | 338.529 | 52.819
13.0625 | 15247 | 345.206 | 55.2486
13.0729 | 14989 | 351.794 | 58.5205
13.0833 | 14647 | 338.589 | 57.7894
13.0938 | 14212 | 326.681 | 55.9646
13.1042 | 14266 | 317.322 | 54.9879
13.1146 | 14126 | 305.764 | 52.0524
13.125 | 13264 | 298.654 | 51.8564
13.1354 | 12636 | 283.361 | 47.9766
13.1458 | 12189 | 276.608 | 45.4481
13.1562 | 11836 | 264.125 | 41.7228
13.1667 | 11481 | 253.269 | 38.5838
13.1771 | 11851 | 244.348 | 36.736
13.1875 | 11540 | 235.974 | 34.9997
13.1979 | 11729 | 229.963 | 32.694
13.2083 | 12450 | 225.821 | 32.7715
13.2188 | 11994 | 223.206 | 32.7946
13.2292 | 12552 | 220.635 | 32.7174
13.2396 | 12755 | 219.725 | 32.6135
13.25 | 12749 | 217.828 | 32.4437
13.2604 | 12030 | 217.397 | 32.3053
13.2708 | 12046 | 217.63 | 32.2152
13.2812 | 11668 | 215.643 | 32.0419
13.2917 | 11810 | 214.125 | 31.7186
13.3021 | 11692 | 213.966 | 31.5665
13.3125 | 11778 | 214.649 | 31.5945
13.3229 | 11994 | 213.705 | 31.6718
13.3333 | 12294 | 213.435 | 31.9941
13.3438 | 12280 | 213.269 | 32.4142
13.3542 | 12162 | 213.185 | 32.7838
13.3646 | 12640 | 215.238 | 33.394
13.375 | 12962 | 217.104 | 34.1071
13.3854 | 14903 | 221.997 | 37.2643
13.3958 | 14903 | 238.126 | 43.6203
13.4062 | 17608 | 265.681 | 50.4294
13.4167 | 19748 | 288.665 | 55.9379
13.4271 | 19370 | 317.918 | 63.6591
13.4375 | 20596 | 345.785 | 69.0288
13.4479 | 21592 | 374.034 | 73.7682
13.4583 | 22891 | 399.399 | 76.3136
13.4688 | 23068 | 416.261 | 76.5079
13.4792 | 23077 | 424.12 | 73.1623
13.4896 | 22905 | 426.867 | 68.0025
13.5 | 20762 | 429.12 | 65.6899
13.5104 | 20005 | 429.274 | 63.1283
13.5208 | 20005 | 419.678 | 59.6768
13.5312 | 19379 | 410.599 | 56.7522
13.5417 | 19339 | 401.486 | 54.6182
13.5521 | 17601 | 395.896 | 52.9966
13.5625 | 19939 | 391.3 | 52.4411
13.5729 | 19576 | 384.906 | 51.3064
13.5833 | 18681 | 385.221 | 50.6582
13.5938 | 18173 | 384.074 | 50.7412
13.6042 | 16574 | 381.34 | 49.8416
13.6146 | 15545 | 376.127 | 49.3228
13.625 | 19259 | 368.552 | 48.2172
13.6354 | 17980 | 361.503 | 47.2342
13.6458 | 17030 | 355.44 | 46.8131
13.6562 | 17669 | 351.76 | 47.1508
13.6667 | 15264 | 348.452 | 47.2093
13.6771 | 14826 | 345.533 | 46.873
13.6875 | 15846 | 343.854 | 47.299
13.6979 | 15819 | 342.747 | 48.3049
13.7083 | 16069 | 338.081 | 48.0123
13.7188 | 15719 | 332.083 | 47.0043
13.7292 | 15418 | 323.696 | 45.2919
13.7396 | 15266 | 319.073 | 44.8557
13.75 | 15459 | 316.907 | 44.7646
13.7604 | 15528 | 323.517 | 46.0334
13.7708 | 15531 | 327.252 | 47.1876
13.7812 | 15524 | 332.832 | 48.5483
13.7917 | 18062 | 332.175 | 50.1097
13.8021 | 17708 | 329.891 | 49.8971
13.8125 | 17440 | 323.65 | 47.0883
13.8229 | 17701 | 325.33 | 49.0408
13.8333 | 15656 | 330.898 | 49.1948
13.8438 | 16676 | 338.019 | 50.2296
13.8542 | 18646 | 345.666 | 52.8482
13.8646 | 17726 | 356.327 | 55.141
13.875 | 17889 | 356.764 | 55.7966
13.8854 | 17311 | 354.572 | 57.066
13.8958 | 15773 | 357.441 | 57.5921
13.9062 | 19830 | 369.355 | 58.6288
13.9167 | 18631 | 372.87 | 58.2234
13.9271 | 18051 | 374.18 | 58.434
13.9375 | 17665 | 375.615 | 58.3352
13.9479 | 14880 | 370.46 | 57.3949
13.9583 | 19617 | 376.895 | 57.7698
13.9688 | 18161 | 378.534 | 56.7891
13.9792 | 18646 | 376.09 | 55.1058
13.9896 | 17683 | 373.579 | 53.5013
14 | 16297 | 370.197 | 52.2749

## Storm Influent
Stom Influent
Time | Flow rate | Total COD | Total Kjeldahl nitrogen (TKN)
d | m3/d | g COD/m3 | g N/m3
0 | 18446 | 381.19 | 54.4256
0.010417 | 18446 | 381.19 | 54.4256
0.020833 | 18446 | 381.19 | 54.4256
0.03125 | 18446 | 381.19 | 54.4256
0.041667 | 18446 | 381.19 | 54.4256
0.052083 | 18446 | 381.19 | 54.4256
0.0625 | 18446 | 381.19 | 54.4256
0.072917 | 18446 | 381.19 | 54.4256
0.083333 | 18446 | 381.19 | 54.4256
0.09375 | 18446 | 381.19 | 54.4256
0.10417 | 18446 | 381.19 | 54.4256
0.11458 | 18446 | 381.19 | 54.4256
0.125 | 18446 | 381.19 | 54.4256
0.13542 | 18446 | 381.19 | 54.4256
0.14583 | 18446 | 381.19 | 54.4256
0.15625 | 18446 | 381.19 | 54.4256
0.16667 | 18446 | 381.19 | 54.4256
0.17708 | 18446 | 381.19 | 54.4256
0.1875 | 18446 | 381.19 | 54.4256
0.19792 | 18446 | 381.19 | 54.4256
0.20833 | 18446 | 381.19 | 54.4256
0.21875 | 18446 | 381.19 | 54.4256
0.22917 | 18446 | 381.19 | 54.4256
0.23958 | 18446 | 381.19 | 54.4256
0.25 | 18446 | 381.19 | 54.4256
0.26042 | 18446 | 381.19 | 54.4256
0.27083 | 18446 | 381.19 | 54.4256
0.28125 | 18446 | 381.19 | 54.4256
0.29167 | 18446 | 381.19 | 54.4256
0.30208 | 18446 | 381.19 | 54.4256
0.3125 | 18446 | 381.19 | 54.4256
0.32292 | 18446 | 381.19 | 54.4256
0.33333 | 18446 | 381.19 | 54.4256
0.34375 | 18446 | 381.19 | 54.4256
0.35417 | 18446 | 381.19 | 54.4256
0.36458 | 18446 | 381.19 | 54.4256
0.375 | 18446 | 381.19 | 54.4256
0.38542 | 18446 | 381.19 | 54.4256
0.39583 | 18446 | 381.19 | 54.4256
0.40625 | 18446 | 381.19 | 54.4256
0.41667 | 18446 | 381.19 | 54.4256
0.42708 | 18446 | 381.19 | 54.4256
0.4375 | 18446 | 381.19 | 54.4256
0.44792 | 18446 | 381.19 | 54.4256
0.45833 | 18446 | 381.19 | 54.4256
0.46875 | 18446 | 381.19 | 54.4256
0.47917 | 18446 | 381.19 | 54.4256
0.48958 | 18446 | 381.19 | 54.4256
0.5 | 18446 | 381.19 | 54.4256
0.51042 | 18446 | 381.19 | 54.4256
0.52083 | 18446 | 381.19 | 54.4256
0.53125 | 18446 | 381.19 | 54.4256
0.54167 | 18446 | 381.19 | 54.4256
0.55208 | 18446 | 381.19 | 54.4256
0.5625 | 18446 | 381.19 | 54.4256
0.57292 | 18446 | 381.19 | 54.4256
0.58333 | 18446 | 381.19 | 54.4256
0.59375 | 18446 | 381.19 | 54.4256
0.60417 | 18446 | 381.19 | 54.4256
0.61458 | 18446 | 381.19 | 54.4256
0.625 | 18446 | 381.19 | 54.4256
0.63542 | 18446 | 381.19 | 54.4256
0.64583 | 18446 | 381.19 | 54.4256
0.65625 | 18446 | 381.19 | 54.4256
0.66667 | 18446 | 381.19 | 54.4256
0.67708 | 18446 | 381.19 | 54.4256
0.6875 | 18446 | 381.19 | 54.4256
0.69792 | 18446 | 381.19 | 54.4256
0.70833 | 18446 | 381.19 | 54.4256
0.71875 | 18446 | 381.19 | 54.4256
0.72917 | 18446 | 381.19 | 54.4256
0.73958 | 18446 | 381.19 | 54.4256
0.75 | 18446 | 381.19 | 54.4256
0.76042 | 18446 | 381.19 | 54.4256
0.77083 | 18446 | 381.19 | 54.4256
0.78125 | 18446 | 381.19 | 54.4256
0.79167 | 18446 | 381.19 | 54.4256
0.80208 | 18446 | 381.19 | 54.4256
0.8125 | 18446 | 381.19 | 54.4256
0.82292 | 18446 | 381.19 | 54.4256
0.83333 | 18446 | 381.19 | 54.4256
0.84375 | 18446 | 381.19 | 54.4256
0.85417 | 18446 | 381.19 | 54.4256
0.86458 | 18446 | 381.19 | 54.4256
0.875 | 18446 | 381.19 | 54.4256
0.88542 | 18446 | 381.19 | 54.4256
0.89583 | 18446 | 381.19 | 54.4256
0.90625 | 18446 | 381.19 | 54.4256
0.91667 | 18446 | 381.19 | 54.4256
0.92708 | 18446 | 381.19 | 54.4256
0.9375 | 18446 | 381.19 | 54.4256
0.94792 | 18446 | 381.19 | 54.4256
0.95833 | 18446 | 381.19 | 54.4256
0.96875 | 18446 | 381.19 | 54.4256
0.97917 | 18446 | 381.19 | 54.4256
0.98958 | 18446 | 381.19 | 54.4256
1 | 18446 | 381.19 | 54.4256
1.0104 | 21477 | 407.888 | 54.4477
1.0208 | 21474 | 405.876 | 54.2134
1.0312 | 19620 | 399.989 | 54.459
1.0417 | 19334 | 394.865 | 54.7791
1.0521 | 18978 | 391.764 | 56.1506
1.0625 | 18321 | 388.441 | 57.9835
1.0729 | 17855 | 398.902 | 61.44
1.0833 | 17237 | 388.491 | 60.8013
1.0938 | 16453 | 375.328 | 58.8441
1.1042 | 16548 | 365.261 | 57.8283
1.1146 | 16295 | 353.352 | 54.8499
1.125 | 14743 | 341.929 | 54.3292
1.1354 | 13613 | 320.789 | 50.0567
1.1458 | 12807 | 308.975 | 47.2124
1.1562 | 12173 | 292.417 | 43.2385
1.1667 | 11533 | 276.711 | 39.8136
1.1771 | 12198 | 266.791 | 37.9423
1.1875 | 11640 | 256.39 | 36.0751
1.1979 | 11978 | 247.469 | 33.6304
1.2083 | 13272 | 246.049 | 33.9027
1.2188 | 12452 | 242.006 | 33.8172
1.2292 | 13453 | 240.775 | 33.8491
1.2396 | 13815 | 241.083 | 33.8235
1.25 | 13803 | 240.417 | 33.7177
1.2604 | 12514 | 236.456 | 33.3425
1.2708 | 12542 | 233.436 | 33.0819
1.2812 | 11865 | 228.794 | 32.7439
1.2917 | 12118 | 225.718 | 32.3476
1.3021 | 11906 | 222.562 | 32.0317
1.3125 | 12059 | 220.665 | 31.9288
1.3229 | 12446 | 220.054 | 32.035
1.3333 | 12982 | 220.996 | 32.4382
1.3438 | 12956 | 221.556 | 32.8963
1.3542 | 12745 | 221.863 | 33.279
1.3646 | 13597 | 224.497 | 33.9482
1.375 | 14171 | 229.249 | 34.8342
1.3854 | 17637 | 242.485 | 38.5683
1.3958 | 17635 | 264.33 | 45.2445
1.4062 | 22461 | 298.601 | 52.6709
1.4167 | 26276 | 337.077 | 59.3146
1.4271 | 25598 | 375.399 | 67.5695
1.4375 | 27780 | 413.696 | 73.7549
1.4479 | 29551 | 452.36 | 79.3185
1.4583 | 31861 | 486.992 | 82.7018
1.4688 | 32171 | 512.038 | 83.4994
1.4792 | 32180 | 527.073 | 80.6567
1.4896 | 31869 | 534.619 | 75.81
1.5 | 28047 | 530.642 | 72.75
1.5104 | 26695 | 523.226 | 69.6171
1.5208 | 26690 | 514.116 | 66.1858
1.5312 | 25572 | 503.532 | 63.0473
1.5417 | 25496 | 496.76 | 61.0326
1.5521 | 22401 | 482.346 | 58.5819
1.5625 | 26555 | 487.172 | 58.9773
1.5729 | 25905 | 488.184 | 58.195
1.5833 | 24310 | 483.723 | 57.1048
1.5938 | 23404 | 478.181 | 56.8375
1.6042 | 20560 | 463.806 | 54.9949
1.6146 | 18732 | 443.922 | 53.4854
1.625 | 25320 | 451.218 | 53.7974
1.6354 | 23046 | 445.711 | 52.6884
1.6458 | 21357 | 436.331 | 51.9173
1.6562 | 22487 | 433.833 | 52.4165
1.6667 | 18221 | 417.816 | 51.3896
1.6771 | 17442 | 402.053 | 50.2784
1.6875 | 19246 | 397.534 | 50.6768
1.6979 | 19197 | 394.731 | 51.5775
1.7083 | 19637 | 392.367 | 51.438
1.7188 | 19014 | 386.358 | 50.3781
1.7292 | 18480 | 376.467 | 48.5382
1.7396 | 18208 | 368.187 | 47.8768
1.75 | 18547 | 364.455 | 47.7201
1.7604 | 18666 | 363.648 | 48.5922
1.7708 | 18670 | 363.481 | 49.5323
1.7812 | 18654 | 364.512 | 50.6435
1.7917 | 23137 | 376.541 | 53.2088
1.8021 | 22509 | 383.808 | 53.4959
1.8125 | 22031 | 388.158 | 51.2444
1.8229 | 22489 | 398.101 | 53.6974
1.8333 | 18876 | 391.676 | 52.9121
1.8438 | 20674 | 394.139 | 53.8252
1.8542 | 24145 | 409.78 | 57.1671
1.8646 | 22518 | 417.213 | 59.1662
1.875 | 22803 | 423.276 | 60.1627
1.8854 | 21780 | 426.09 | 61.6271
1.8958 | 19067 | 420.05 | 61.4411
1.9062 | 26211 | 439.142 | 63.4723
1.9167 | 24096 | 445.193 | 63.0493
1.9271 | 23071 | 445.77 | 63.1374
1.9375 | 22388 | 443.7 | 62.7882
1.9479 | 17483 | 424.981 | 60.6968
1.9583 | 25814 | 438.815 | 62.1558
1.9688 | 23248 | 438.995 | 60.8936
1.9792 | 24098 | 440.224 | 59.4942
1.9896 | 22402 | 435.94 | 57.6492
2 | 19962 | 424.663 | 55.7787
2.0104 | 18363 | 408.694 | 54.052
2.0208 | 18618 | 398.5 | 53.4005
2.0312 | 19046 | 393.304 | 54.0072
2.0417 | 23433 | 403.839 | 55.8547
2.0521 | 22011 | 408.218 | 57.494
2.0625 | 23310 | 417.413 | 60.3042
2.0729 | 23158 | 425.681 | 63.6884
2.0833 | 15122 | 402.222 | 61.2692
2.0938 | 15319 | 383.34 | 59.1361
2.1042 | 15342 | 368.602 | 57.8633
2.1146 | 14751 | 351.82 | 54.5867
2.125 | 14287 | 339.78 | 54.1525
2.1354 | 12478 | 319.354 | 49.86
2.1458 | 12477 | 306.971 | 47.0735
2.1562 | 11347 | 288.387 | 42.9492
2.1667 | 11037 | 272.158 | 39.5317
2.1771 | 10473 | 258.031 | 37.3391
2.1875 | 10000 | 244.708 | 35.3368
2.1979 | 11258 | 236.118 | 32.9808
2.2083 | 10436 | 228.58 | 32.7738
2.2188 | 10976 | 223.715 | 32.7517
2.2292 | 11250 | 219.452 | 32.5681
2.2396 | 11740 | 217.583 | 32.4337
2.25 | 11562 | 214.543 | 32.1932
2.2604 | 12124 | 213.759 | 32.1206
2.2708 | 12578 | 214.146 | 32.0669
2.2812 | 11399 | 210.837 | 31.7729
2.2917 | 11448 | 208.333 | 31.3924
2.3021 | 12090 | 208.104 | 31.2848
2.3125 | 12429 | 209.075 | 31.3432
2.3229 | 11500 | 207.25 | 31.3021
2.3333 | 11717 | 206.549 | 31.5962
2.3438 | 11751 | 206.058 | 32.0029
2.3542 | 11489 | 205.392 | 32.3335
2.3646 | 12859 | 208.553 | 33.0545
2.375 | 12350 | 210.671 | 33.7289
2.3854 | 12194 | 215.612 | 36.7544
2.3958 | 15329 | 235.446 | 43.5039
2.4062 | 22901 | 274.793 | 51.3433
2.4167 | 23690 | 308.419 | 57.3952
2.4271 | 24749 | 348.238 | 65.8922
2.4375 | 27249 | 388.599 | 72.1988
2.4479 | 29504 | 430.668 | 78.0024
2.4583 | 31868 | 471.119 | 81.7277
2.4688 | 32126 | 501.093 | 82.8183
2.4792 | 31909 | 519.703 | 80.1568
2.4896 | 31927 | 531.491 | 75.6282
2.5 | 31719 | 540.931 | 74.0521
2.5104 | 30926 | 545.833 | 71.7672
2.5208 | 27039 | 534.318 | 67.4463
2.5312 | 25844 | 522.549 | 64.2129
2.5417 | 25174 | 510.637 | 61.7857
2.5521 | 24783 | 502.414 | 60.1625
2.5625 | 24444 | 495.288 | 59.0782
2.5729 | 22762 | 484.346 | 57.4214
2.5833 | 24940 | 484.59 | 57.265
2.5938 | 24113 | 481.797 | 57.1685
2.6042 | 23320 | 476.538 | 56.1816
2.6146 | 22247 | 467.756 | 55.3931
2.625 | 21875 | 456.89 | 53.5683
2.6354 | 21863 | 447.211 | 52.5854
2.6458 | 21236 | 438.046 | 51.9954
2.6562 | 21473 | 432.225 | 52.1679
2.6667 | 20822 | 426.133 | 52.2435
2.6771 | 20463 | 420.443 | 51.7378
2.6875 | 20034 | 415.884 | 51.8146
2.6979 | 19328 | 411.428 | 52.5268
2.7083 | 18928 | 403.512 | 51.963
2.7188 | 18510 | 394.292 | 50.7516
2.7292 | 18319 | 383.021 | 48.8802
2.7396 | 18224 | 375.88 | 48.3042
2.75 | 19106 | 372.828 | 48.2561
2.7604 | 22491 | 383.189 | 50.1835
2.7708 | 21604 | 388.29 | 51.3022
2.7812 | 22228 | 395.84 | 52.8685
2.7917 | 21169 | 395.293 | 54.0189
2.8021 | 19849 | 391.428 | 53.5739
2.8125 | 17451 | 380.798 | 50.2297
2.8229 | 18335 | 380.482 | 52.1583
2.8333 | 22018 | 389.449 | 53.2015
2.8438 | 23369 | 400.713 | 54.5625
2.8542 | 23270 | 411.344 | 57.1358
2.8646 | 25050 | 426.904 | 60.0867
2.875 | 21540 | 426.313 | 60.1557
2.8854 | 19321 | 420.609 | 60.9716
2.8958 | 21190 | 423.674 | 61.94
2.9062 | 26591 | 443.175 | 63.766
2.9167 | 24225 | 448.869 | 63.2817
2.9271 | 23902 | 451.657 | 63.6024
2.9375 | 24339 | 455.04 | 63.7376
2.9479 | 21529 | 447.472 | 62.5471
2.9583 | 26978 | 460.136 | 63.5921
2.9688 | 25693 | 464.394 | 62.75
2.9792 | 24779 | 462.814 | 60.9137
2.9896 | 24086 | 460.173 | 59.3081
3 | 23308 | 455.71 | 58.0591
3.0104 | 21017 | 442.197 | 56.3229
3.0208 | 21014 | 433.315 | 55.7001
3.0312 | 19118 | 405.874 | 54.7171
3.0417 | 18847 | 406.265 | 55.3463
3.0521 | 18509 | 402.748 | 56.6966
3.0625 | 17886 | 400.461 | 58.5895
3.0729 | 17445 | 399.241 | 61.4038
3.0833 | 16858 | 392.979 | 60.998
3.0938 | 16116 | 396.435 | 59.9494
3.1042 | 16206 | 383.436 | 58.7755
3.1146 | 15965 | 368.325 | 55.624
3.125 | 14494 | 359.929 | 55.256
3.1354 | 13423 | 344.187 | 51.2798
3.1458 | 12660 | 333.85 | 48.5108
3.1562 | 12059 | 317.058 | 44.5218
3.1667 | 11453 | 300.831 | 41.0665
3.1771 | 12083 | 286.664 | 38.9763
3.1875 | 11554 | 272.898 | 36.9313
3.1979 | 11875 | 262.401 | 34.4051
3.2083 | 13101 | 254.173 | 34.3196
3.2188 | 12323 | 248.221 | 34.1344
3.2292 | 13271 | 246.103 | 34.1179
3.2396 | 13614 | 242.043 | 33.8593
3.25 | 13604 | 240.755 | 33.7205
3.2604 | 12382 | 240.733 | 33.5579
3.2708 | 12408 | 240.457 | 33.4419
3.2812 | 11767 | 236.243 | 33.1272
3.2917 | 12006 | 233.013 | 32.7228
3.3021 | 11805 | 228.517 | 32.3369
3.3125 | 11951 | 225.931 | 32.1978
3.3229 | 12317 | 223.087 | 32.186
3.3333 | 12825 | 221.208 | 32.4388
3.3438 | 12800 | 220.628 | 32.8367
3.3542 | 12600 | 221.957 | 33.2743
3.3646 | 13408 | 222.805 | 33.8454
3.375 | 13952 | 223.935 | 34.5353
3.3854 | 17235 | 230.837 | 37.8998
3.3958 | 17233 | 245.177 | 44.1624
3.4062 | 21804 | 265.157 | 50.7094
3.4167 | 25418 | 284.426 | 56.1452
3.4271 | 24776 | 322.005 | 64.3669
3.4375 | 26842 | 362.795 | 70.6257
3.4479 | 28519 | 395.642 | 75.7769
3.4583 | 30707 | 427.852 | 78.9244
3.4688 | 31000 | 456.023 | 79.8887
3.4792 | 31009 | 478.98 | 77.5178
3.4896 | 30713 | 495.397 | 73.2117
3.5 | 27093 | 509.635 | 71.3304
3.5104 | 25812 | 520.396 | 69.2902
3.5208 | 25808 | 516.967 | 66.1932
3.5312 | 24748 | 510.469 | 63.3038
3.5417 | 24677 | 503.054 | 61.2526
3.5521 | 21745 | 495.89 | 59.2389
3.5625 | 25678 | 493.274 | 59.1813
3.5729 | 25062 | 480.696 | 57.6096
3.5833 | 23552 | 487.077 | 57.1665
3.5938 | 22693 | 489.366 | 57.3571
3.6042 | 20001 | 485.226 | 56.1045
3.6146 | 18269 | 478.271 | 55.3135
3.625 | 24508 | 460.124 | 54.1848
3.6354 | 22354 | 437.134 | 52.0879
3.6458 | 20755 | 445.688 | 52.3514
3.6562 | 21824 | 442.89 | 52.8291
3.6667 | 17785 | 435.839 | 52.3181
3.6771 | 17047 | 434.983 | 52.0264
3.6875 | 18755 | 420.746 | 51.8984
3.6979 | 18708 | 407.608 | 52.2267
3.7083 | 19125 | 400.63 | 51.8299
3.7188 | 18535 | 392.776 | 50.6709
3.7292 | 18029 | 386.203 | 49.0176
3.7396 | 17772 | 380.609 | 48.5062
3.75 | 18093 | 374.177 | 48.2004
3.7604 | 18205 | 368.454 | 48.8008
3.7708 | 18209 | 367.506 | 49.6981
3.7812 | 18193 | 368.129 | 50.7872
3.7917 | 22437 | 365.306 | 52.4768
3.8021 | 21842 | 363.401 | 52.2468
3.8125 | 21390 | 376.101 | 50.4751
3.8229 | 21824 | 387.915 | 53.0273
3.8333 | 18403 | 393.24 | 52.936
3.8438 | 20104 | 400.066 | 54.0822
3.8542 | 23390 | 396.287 | 56.285
3.8646 | 21850 | 401.222 | 58.1621
3.875 | 22120 | 415.236 | 59.6069
3.8854 | 21151 | 421.553 | 61.2809
3.8958 | 18582 | 428.336 | 61.8336
3.9062 | 25345 | 429.74 | 62.7955
3.9167 | 23343 | 421.569 | 61.5765
3.9271 | 22372 | 438.576 | 62.6217
3.9375 | 21725 | 442.859 | 62.6414
3.9479 | 17083 | 442.424 | 61.5956
3.9583 | 24968 | 439.346 | 62.0608
3.9688 | 22540 | 420.363 | 59.7208
3.9792 | 23343 | 432.824 | 58.9531
3.9896 | 21738 | 432.716 | 57.3653
4 | 19429 | 435.736 | 56.3185
4.0104 | 17915 | 430.006 | 55.1639
4.0208 | 18156 | 418.73 | 54.4548
4.0312 | 18561 | 406.677 | 54.6829
4.0417 | 22713 | 398.89 | 55.4701
4.0521 | 21366 | 396.066 | 56.714
4.0625 | 22596 | 409.429 | 59.7443
4.0729 | 22452 | 415.684 | 63.0138
4.0833 | 14847 | 421.931 | 62.2919
4.0938 | 15033 | 423.196 | 61.2462
4.1042 | 15055 | 397.158 | 59.3666
4.1146 | 14496 | 376.33 | 55.8711
4.125 | 14056 | 363.267 | 55.3815
4.1354 | 12345 | 342.654 | 51.0726
4.1458 | 12344 | 331.926 | 48.374
4.1562 | 11274 | 315.622 | 44.3631
4.1667 | 10981 | 298.828 | 40.9146
4.1771 | 10448 | 282.636 | 38.6115
4.1875 | 10000 | 268.347 | 36.5564
4.1979 | 11190 | 253.645 | 33.8895
4.2083 | 10412 | 242.497 | 33.4927
4.2188 | 10923 | 236.877 | 33.4326
4.2292 | 11182 | 228.643 | 33.0427
4.2396 | 11646 | 223.762 | 32.7509
4.25 | 11478 | 219.443 | 32.4438
4.2604 | 12009 | 217.245 | 32.2963
4.2708 | 12439 | 214.596 | 32.0816
4.2812 | 11323 | 213.56 | 31.9103
4.2917 | 11370 | 213.733 | 31.6695
4.3021 | 11977 | 210.569 | 31.4071
4.3125 | 12298 | 208.554 | 31.3075
4.3229 | 11419 | 208.637 | 31.3696
4.3333 | 11624 | 209.623 | 31.7514
4.3438 | 11656 | 207.83 | 32.0899
4.3542 | 11409 | 207.518 | 32.4396
4.3646 | 12704 | 207.316 | 32.9798
4.375 | 12223 | 207.473 | 33.5528
4.3854 | 12076 | 214.902 | 36.7098
4.3958 | 15040 | 226.609 | 43.0091
4.4062 | 22202 | 238.297 | 49.2054
4.4167 | 22948 | 255.559 | 54.2937
4.4271 | 23950 | 298.211 | 62.9167
4.4375 | 26314 | 334.153 | 68.8837
4.4479 | 28447 | 368.497 | 74.1429
4.4583 | 30682 | 402.767 | 77.3937
4.4688 | 30926 | 434.341 | 78.5557
4.4792 | 30720 | 463.112 | 76.5074
4.4896 | 30737 | 484.454 | 72.5488
4.5 | 30540 | 502.265 | 71.4789
4.5104 | 29790 | 517.266 | 69.8204
4.5208 | 26113 | 527.245 | 66.8538
4.5312 | 24983 | 533.06 | 64.6646
4.5417 | 24349 | 523.24 | 62.3652
4.5521 | 23979 | 514.893 | 60.7388
4.5625 | 23658 | 507.141 | 59.6219
4.5729 | 22068 | 500.749 | 58.2357
4.5833 | 24127 | 495.185 | 57.7373
4.5938 | 23345 | 485.528 | 57.2508
4.6042 | 22595 | 486.089 | 56.6052
4.6146 | 21580 | 481.879 | 56.0845
4.625 | 21228 | 472.845 | 54.3669
4.6354 | 21217 | 460.952 | 53.2603
4.6458 | 20623 | 451.353 | 52.6496
4.6562 | 20848 | 444.386 | 52.7581
4.6667 | 20232 | 437.551 | 52.7958
4.6771 | 19893 | 433.371 | 52.3776
4.6875 | 19487 | 429.056 | 52.4707
4.6979 | 18819 | 425.985 | 53.2633
4.7083 | 18441 | 418.967 | 52.7516
4.7188 | 18045 | 409.461 | 51.5264
4.7292 | 17864 | 397.339 | 49.6095
4.7396 | 17775 | 388.533 | 48.9431
4.75 | 18608 | 380.723 | 48.63
4.7604 | 21808 | 376.141 | 49.6919
4.7708 | 20969 | 375.871 | 50.5151
4.7812 | 21559 | 387.657 | 52.3127
4.7917 | 20558 | 390.1 | 53.6431
4.8021 | 19310 | 394.71 | 53.6844
4.8125 | 17043 | 394.839 | 50.9456
4.8229 | 17878 | 395.529 | 52.9297
4.8333 | 21360 | 385.882 | 52.9126
4.8438 | 22636 | 382.453 | 53.4169
4.8542 | 22542 | 394.058 | 56.0451
4.8646 | 24225 | 407.791 | 58.859
4.875 | 20907 | 416.799 | 59.5274
4.8854 | 18809 | 431.235 | 61.4905
4.8958 | 20576 | 431.369 | 62.2877
4.9062 | 25680 | 424.259 | 62.5217
4.9167 | 23444 | 425.189 | 61.7991
4.9271 | 23139 | 442.605 | 62.9656
4.9375 | 23551 | 446.529 | 63.125
4.9479 | 20895 | 448.304 | 62.4979
4.9583 | 26044 | 450.677 | 62.8878
4.9688 | 24830 | 442.837 | 61.3546
4.9792 | 23966 | 454.13 | 60.2791
4.9896 | 23311 | 458.097 | 59.0628
5 | 22576 | 458.31 | 58.09
5.0104 | 20411 | 454.219 | 56.9043
5.0208 | 20408 | 449.755 | 56.532
5.0312 | 18616 | 399.989 | 54.3197
5.0417 | 18359 | 394.865 | 54.6463
5.0521 | 18040 | 391.764 | 56.0252
5.0625 | 17452 | 388.442 | 57.8699
5.0729 | 17034 | 398.901 | 61.3303
5.0833 | 16480 | 388.491 | 60.7039
5.0938 | 15778 | 375.328 | 58.7604
5.1042 | 15863 | 365.261 | 57.7457
5.1146 | 15636 | 353.352 | 54.7727
5.125 | 14246 | 341.704 | 54.2509
5.1354 | 13234 | 320.789 | 50.0164
5.1458 | 12513 | 308.975 | 47.1827
5.1562 | 11946 | 292.417 | 43.2167
5.1667 | 11373 | 276.711 | 39.7991
5.1771 | 11968 | 266.792 | 37.9224
5.1875 | 11468 | 256.391 | 36.061
5.1979 | 11771 | 247.469 | 33.6139
5.2083 | 12929 | 246.049 | 33.8756
5.2188 | 12195 | 242.005 | 33.7973
5.2292 | 13090 | 240.775 | 33.8213
5.2396 | 13414 | 241.083 | 33.7928
5.25 | 13404 | 240.418 | 33.6872
5.2604 | 12250 | 236.456 | 33.3228
5.2708 | 12275 | 233.437 | 33.0623
5.2812 | 11669 | 228.794 | 32.7299
5.2917 | 11895 | 225.718 | 32.332
5.3021 | 11705 | 222.563 | 32.018
5.3125 | 11843 | 220.665 | 31.9141
5.3229 | 12189 | 220.054 | 32.0177
5.3333 | 12669 | 220.996 | 32.417
5.3438 | 12645 | 221.556 | 32.8752
5.3542 | 12456 | 221.863 | 33.2595
5.3646 | 13219 | 224.498 | 33.9223
5.375 | 13732 | 229.249 | 34.8035
5.3854 | 16832 | 242.485 | 38.509
5.3958 | 16830 | 264.33 | 45.1813
5.4062 | 21148 | 298.6 | 52.5543
5.4167 | 24560 | 337.077 | 59.1392
5.4271 | 23953 | 375.399 | 67.384
5.4375 | 25904 | 413.696 | 73.5203
5.4479 | 27488 | 452.36 | 79.0332
5.4583 | 29553 | 486.992 | 82.3518
5.4688 | 29829 | 512.038 | 83.1169
5.4792 | 29837 | 527.074 | 80.2509
5.4896 | 29558 | 534.619 | 75.3918
5.5 | 26139 | 530.642 | 72.4017
5.5104 | 24930 | 523.226 | 69.2956
5.5208 | 24925 | 514.117 | 65.8659
5.5312 | 23924 | 503.532 | 62.7525
5.5417 | 23857 | 496.759 | 60.74
5.5521 | 21088 | 482.346 | 58.3551
5.5625 | 24802 | 487.172 | 58.6696
5.5729 | 24220 | 488.185 | 57.8984
5.5833 | 22794 | 483.723 | 56.8411
5.5938 | 21983 | 478.182 | 56.5947
5.6042 | 19441 | 463.805 | 54.811
5.6146 | 17806 | 443.922 | 53.3414
5.625 | 23695 | 451.218 | 53.5371
5.6354 | 21662 | 445.711 | 52.4679
5.6458 | 20152 | 436.331 | 51.7294
5.6562 | 21161 | 433.833 | 52.2108
5.6667 | 17348 | 417.816 | 51.2606
5.6771 | 16651 | 402.052 | 50.1675
5.6875 | 18264 | 397.534 | 50.542
5.6979 | 18220 | 394.731 | 51.4461
5.7083 | 18613 | 392.367 | 51.3012
5.7188 | 18056 | 386.359 | 50.2521
5.7292 | 17578 | 376.468 | 48.4219
5.7396 | 17335 | 368.187 | 47.7669
5.75 | 17638 | 364.455 | 47.6067
5.7604 | 17744 | 363.648 | 48.4781
5.7708 | 17747 | 363.481 | 49.4189
5.7812 | 17733 | 364.512 | 50.531
5.7917 | 21738 | 376.541 | 53.0299
5.8021 | 21176 | 383.808 | 53.321
5.8125 | 20749 | 388.158 | 51.0735
5.8229 | 21158 | 398.101 | 53.5167
5.8333 | 17930 | 391.676 | 52.7867
5.8438 | 19535 | 394.139 | 53.6737
5.8542 | 22636 | 409.78 | 56.9579
5.8646 | 21182 | 417.213 | 58.9788
5.875 | 21436 | 423.276 | 59.9684
5.8854 | 20522 | 426.09 | 61.4483
5.8958 | 18098 | 420.05 | 61.3071
5.9062 | 24479 | 439.141 | 63.2187
5.9167 | 22590 | 445.192 | 62.8249
5.9271 | 21673 | 445.769 | 62.9284
5.9375 | 21063 | 443.699 | 62.5904
5.9479 | 16683 | 424.981 | 60.5834
5.9583 | 24122 | 438.815 | 61.9038
5.9688 | 21831 | 438.995 | 60.6809
5.9792 | 22589 | 440.223 | 59.2643
5.9896 | 21074 | 435.94 | 57.4481
6 | 18895 | 424.663 | 55.6216
6.0104 | 16990 | 338.279 | 50.0027
6.0208 | 16990 | 331.66 | 49.5169
6.0312 | 15964 | 328.748 | 50.085
6.0417 | 15806 | 334.966 | 51.0517
6.0521 | 15610 | 338.529 | 52.8192
6.0625 | 15247 | 345.206 | 55.2488
6.0729 | 14989 | 351.794 | 58.521
6.0833 | 14647 | 338.589 | 57.789
6.0938 | 14212 | 326.681 | 55.9643
6.1042 | 14266 | 317.322 | 54.9879
6.1146 | 14126 | 305.764 | 52.0521
6.125 | 13264 | 298.654 | 51.8563
6.1354 | 12636 | 283.361 | 47.9771
6.1458 | 12189 | 276.608 | 45.4481
6.1562 | 11836 | 264.125 | 41.7233
6.1667 | 11481 | 253.269 | 38.5836
6.1771 | 11851 | 244.348 | 36.7356
6.1875 | 11540 | 235.974 | 34.9994
6.1979 | 11729 | 229.963 | 32.6937
6.2083 | 12450 | 225.821 | 32.7718
6.2188 | 11994 | 223.206 | 32.795
6.2292 | 12552 | 220.635 | 32.7178
6.2396 | 12755 | 219.725 | 32.6139
6.25 | 12749 | 217.828 | 32.4436
6.2604 | 12030 | 217.397 | 32.3056
6.2708 | 12046 | 217.63 | 32.2154
6.2812 | 11668 | 215.643 | 32.0415
6.2917 | 11810 | 214.125 | 31.7184
6.3021 | 11692 | 213.966 | 31.567
6.3125 | 11778 | 214.649 | 31.5946
6.3229 | 11994 | 213.705 | 31.6714
6.3333 | 12294 | 213.435 | 31.9938
6.3438 | 12280 | 213.269 | 32.4144
6.3542 | 12162 | 213.185 | 32.7836
6.3646 | 12640 | 215.238 | 33.394
6.375 | 12962 | 217.104 | 34.107
6.3854 | 14903 | 221.997 | 37.2646
6.3958 | 14903 | 238.126 | 43.6202
6.4062 | 17608 | 265.681 | 50.4291
6.4167 | 19748 | 288.665 | 55.9374
6.4271 | 19370 | 317.918 | 63.6594
6.4375 | 20596 | 345.785 | 69.0289
6.4479 | 21592 | 374.034 | 73.7686
6.4583 | 22891 | 399.399 | 76.3141
6.4688 | 23068 | 416.261 | 76.5074
6.4792 | 23077 | 424.12 | 73.1621
6.4896 | 22905 | 426.867 | 68.0027
6.5 | 20762 | 429.12 | 65.69
6.5104 | 20005 | 429.274 | 63.1281
6.5208 | 20005 | 419.678 | 59.6764
6.5312 | 19379 | 410.599 | 56.7519
6.5417 | 19339 | 401.486 | 54.6183
6.5521 | 17601 | 395.896 | 52.9963
6.5625 | 19939 | 391.3 | 52.4407
6.5729 | 19576 | 384.906 | 51.3068
6.5833 | 18681 | 385.221 | 50.6586
6.5938 | 18173 | 384.074 | 50.7415
6.6042 | 16574 | 381.34 | 49.8413
6.6146 | 15545 | 376.127 | 49.3229
6.625 | 19259 | 368.552 | 48.2167
6.6354 | 17980 | 361.503 | 47.2343
6.6458 | 17030 | 355.44 | 46.813
6.6562 | 17669 | 351.76 | 47.151
6.6667 | 15264 | 348.452 | 47.2095
6.6771 | 14826 | 345.533 | 46.8725
6.6875 | 15846 | 343.854 | 47.2991
6.6979 | 15819 | 342.747 | 48.3051
6.7083 | 16069 | 338.081 | 48.0124
6.7188 | 15719 | 332.083 | 47.0047
6.7292 | 15418 | 323.696 | 45.2916
6.7396 | 15266 | 319.073 | 44.8559
6.75 | 15459 | 316.907 | 44.765
6.7604 | 15528 | 323.517 | 46.0335
6.7708 | 15531 | 327.252 | 47.1872
6.7812 | 15524 | 332.832 | 48.5481
6.7917 | 18062 | 332.175 | 50.1099
6.8021 | 17708 | 329.891 | 49.8972
6.8125 | 17440 | 323.65 | 47.0884
6.8229 | 17701 | 325.33 | 49.0407
6.8333 | 15656 | 330.898 | 49.1949
6.8438 | 16676 | 338.019 | 50.2292
6.8542 | 18646 | 345.666 | 52.8478
6.8646 | 17726 | 356.327 | 55.1411
6.875 | 17889 | 356.764 | 55.7966
6.8854 | 17311 | 354.572 | 57.0663
6.8958 | 15773 | 357.441 | 57.5925
6.9062 | 19830 | 369.355 | 58.6288
6.9167 | 18631 | 372.87 | 58.2231
6.9271 | 18051 | 374.18 | 58.4337
6.9375 | 17665 | 375.615 | 58.3357
6.9479 | 14880 | 370.46 | 57.3953
6.9583 | 19617 | 376.895 | 57.77
6.9688 | 18161 | 378.534 | 56.7888
6.9792 | 18646 | 376.09 | 55.1057
6.9896 | 17683 | 373.579 | 53.5016
7 | 16297 | 370.197 | 52.2747
7.0104 | 15388 | 360.726 | 51.0389
7.0208 | 15534 | 354.752 | 50.6086
7.0312 | 15779 | 328.749 | 50.0654
7.0417 | 18281 | 334.966 | 51.322
7.0521 | 17472 | 338.529 | 53.0236
7.0625 | 18215 | 345.206 | 55.5791
7.0729 | 18130 | 351.794 | 58.8739
7.0833 | 13548 | 338.589 | 57.6723
7.0938 | 13661 | 326.681 | 55.908
7.1042 | 13676 | 317.322 | 54.9294
7.1146 | 13339 | 305.764 | 51.9767
7.125 | 13075 | 298.653 | 51.8387
7.1354 | 12042 | 283.361 | 47.9237
7.1458 | 12042 | 276.608 | 45.4355
7.1562 | 11397 | 264.124 | 41.6868
7.1667 | 11220 | 253.269 | 38.5629
7.1771 | 10898 | 244.347 | 36.6626
7.1875 | 10627 | 235.973 | 34.9322
7.1979 | 11347 | 229.963 | 32.6662
7.2083 | 10876 | 225.821 | 32.6617
7.2188 | 11186 | 223.206 | 32.7396
7.2292 | 11343 | 220.635 | 32.6361
7.2396 | 11624 | 219.725 | 32.5381
7.25 | 11522 | 217.828 | 32.3623
7.2604 | 11844 | 217.398 | 32.2934
7.2708 | 12105 | 217.63 | 32.2193
7.2812 | 11429 | 215.643 | 32.0258
7.2917 | 11457 | 214.125 | 31.6956
7.3021 | 11826 | 213.966 | 31.5757
7.3125 | 12021 | 214.649 | 31.6104
7.3229 | 11488 | 213.704 | 31.6387
7.3333 | 11613 | 213.435 | 31.9501
7.3438 | 11632 | 213.269 | 32.373
7.3542 | 11482 | 213.184 | 32.7403
7.3646 | 12270 | 215.239 | 33.3702
7.375 | 11978 | 217.105 | 34.0436
7.3854 | 11889 | 221.997 | 37.0703
7.3958 | 13692 | 238.127 | 43.5395
7.4062 | 18050 | 265.682 | 50.4618
7.4167 | 18506 | 288.665 | 55.8376
7.4271 | 19118 | 317.918 | 63.6375
7.4375 | 20560 | 345.785 | 69.0254
7.4479 | 21862 | 374.034 | 73.7964
7.4583 | 23227 | 399.399 | 76.3519
7.4688 | 23379 | 416.261 | 76.5449
7.4792 | 23258 | 424.12 | 73.1851
7.4896 | 23272 | 426.868 | 68.0513
7.5 | 23155 | 429.121 | 66.0179
7.5104 | 22701 | 429.274 | 63.5052
7.5208 | 20461 | 419.677 | 59.7396
7.5312 | 19774 | 410.6 | 56.8062
7.5417 | 19390 | 401.486 | 54.6251
7.5521 | 19166 | 395.896 | 53.206
7.5625 | 18973 | 391.3 | 52.3128
7.5729 | 18003 | 384.906 | 51.1028
7.5833 | 19264 | 385.221 | 50.7342
7.5938 | 18789 | 384.074 | 50.8207
7.6042 | 18332 | 381.34 | 50.065
7.6146 | 17713 | 376.127 | 49.5939
7.625 | 17500 | 368.552 | 48.0004
7.6354 | 17495 | 361.503 | 47.1754
7.6458 | 17134 | 355.44 | 46.8254
7.6562 | 17273 | 351.76 | 47.1043
7.6667 | 16898 | 348.452 | 47.3999
7.6771 | 16692 | 345.533 | 47.0869
7.6875 | 16445 | 343.854 | 47.3669
7.6979 | 16037 | 342.747 | 48.3293
7.7083 | 15806 | 338.081 | 47.9837
7.7188 | 15565 | 332.082 | 46.9882
7.7292 | 15456 | 323.697 | 45.2956
7.7396 | 15402 | 319.073 | 44.87
7.75 | 15915 | 316.907 | 44.8122
7.7604 | 17883 | 323.517 | 46.2825
7.7708 | 17370 | 327.252 | 47.3832
7.7812 | 17735 | 332.832 | 48.7865
7.7917 | 17121 | 332.174 | 50.0083
7.8021 | 16355 | 329.89 | 49.7524
7.8125 | 14962 | 323.651 | 46.8302
7.8229 | 15477 | 325.331 | 48.8117
7.8333 | 17623 | 330.898 | 49.4017
7.8438 | 18411 | 338.02 | 50.4164
7.8542 | 18356 | 345.666 | 52.816
7.8646 | 19395 | 356.327 | 55.3295
7.875 | 17352 | 356.764 | 55.7363
7.8854 | 16060 | 354.572 | 56.9288
7.8958 | 17152 | 357.44 | 57.7444
7.9062 | 20304 | 369.356 | 58.6834
7.9167 | 18926 | 372.87 | 58.2574
7.9271 | 18740 | 374.18 | 58.5145
7.9375 | 18997 | 375.615 | 58.4937
7.9479 | 17359 | 370.46 | 57.6857
7.9583 | 20544 | 376.896 | 57.8823
7.9688 | 19796 | 378.534 | 56.9896
7.9792 | 19265 | 376.091 | 55.1821
7.9896 | 18862 | 373.58 | 53.6471
8 | 18409 | 370.196 | 52.5339
8.0104 | 21477 | 407.888 | 54.4477
8.0208 | 21474 | 405.876 | 54.2134
8.0312 | 19620 | 399.989 | 54.459
8.0417 | 19334 | 394.865 | 54.7791
8.0521 | 18978 | 391.764 | 56.1506
8.0625 | 18321 | 388.441 | 57.9835
8.0729 | 17855 | 398.902 | 61.44
8.0833 | 17237 | 388.491 | 60.8013
8.0938 | 16453 | 375.328 | 58.8441
8.1042 | 16548 | 365.261 | 57.8283
8.1146 | 16295 | 353.352 | 54.8499
8.125 | 14743 | 341.929 | 54.3292
8.1354 | 13613 | 320.789 | 50.0567
8.1458 | 12807 | 308.975 | 47.2124
8.1562 | 12173 | 292.417 | 43.2385
8.1667 | 11533 | 276.711 | 39.8136
8.1771 | 12198 | 266.791 | 37.9423
8.1875 | 11640 | 256.39 | 36.0751
8.1979 | 11978 | 247.469 | 33.6304
8.2083 | 13272 | 246.049 | 33.9027
8.2188 | 12452 | 242.006 | 33.8172
8.2292 | 13453 | 240.775 | 33.8491
8.2396 | 13815 | 241.083 | 33.8235
8.25 | 13803 | 240.417 | 33.7177
8.2604 | 12514 | 236.456 | 33.3425
8.2708 | 12542 | 233.436 | 33.0819
8.2812 | 11865 | 228.794 | 32.7439
8.2917 | 12118 | 225.718 | 32.3476
8.3021 | 11906 | 222.562 | 32.0317
8.3125 | 12059 | 220.665 | 31.9288
8.3229 | 12446 | 220.054 | 32.035
8.3333 | 12982 | 220.996 | 32.4382
8.3438 | 12956 | 221.556 | 32.8963
8.3542 | 12745 | 221.863 | 33.279
8.3646 | 13597 | 224.497 | 33.9482
8.375 | 14171 | 229.249 | 34.8342
8.3854 | 17637 | 242.485 | 38.5683
8.3958 | 17635 | 264.33 | 45.2445
8.4062 | 22461 | 298.601 | 52.6709
8.4167 | 26276 | 337.077 | 59.3146
8.4271 | 25598 | 375.399 | 67.5695
8.4375 | 27780 | 413.696 | 73.7549
8.4479 | 29551 | 452.36 | 79.3185
8.4583 | 31861 | 486.992 | 82.7018
8.4688 | 32171 | 512.038 | 83.4994
8.4792 | 32180 | 527.073 | 80.6567
8.4896 | 31869 | 534.619 | 75.81
8.5 | 28047 | 530.642 | 72.75
8.5104 | 26695 | 523.226 | 69.6171
8.5208 | 26690 | 514.116 | 66.1858
8.5312 | 25572 | 503.532 | 63.0473
8.5417 | 25496 | 496.76 | 61.0326
8.5521 | 22401 | 482.346 | 58.5819
8.5625 | 26555 | 487.172 | 58.9773
8.5729 | 25905 | 488.184 | 58.195
8.5833 | 24310 | 483.723 | 57.1048
8.5938 | 23404 | 478.181 | 56.8375
8.6042 | 20560 | 463.806 | 54.9949
8.6146 | 18732 | 443.922 | 53.4854
8.625 | 25320 | 451.218 | 53.7974
8.6354 | 23046 | 445.711 | 52.6884
8.6458 | 21357 | 436.331 | 51.9173
8.6562 | 22487 | 433.833 | 52.4165
8.6667 | 18221 | 417.816 | 51.3896
8.6771 | 17442 | 402.053 | 50.2784
8.6875 | 19246 | 397.534 | 50.6768
8.6979 | 19197 | 394.731 | 51.5775
8.7083 | 19637 | 392.367 | 51.438
8.7188 | 19014 | 386.358 | 50.3781
8.7292 | 18480 | 376.467 | 48.5382
8.7396 | 18208 | 368.187 | 47.8768
8.75 | 18547 | 364.455 | 47.7201
8.7604 | 18666 | 363.648 | 48.5922
8.7708 | 18670 | 363.481 | 49.5323
8.7812 | 18654 | 364.512 | 50.6435
8.7917 | 23137 | 376.541 | 53.2088
8.8021 | 22509 | 383.808 | 53.4959
8.8125 | 22031 | 388.158 | 51.2444
8.8229 | 22489 | 398.101 | 53.6974
8.8333 | 18876 | 391.676 | 52.9121
8.8438 | 20674 | 394.139 | 53.8252
8.8542 | 24145 | 409.78 | 57.1671
8.8646 | 22518 | 417.213 | 59.1662
8.875 | 22803 | 423.276 | 60.1627
8.8854 | 21780 | 426.09 | 61.6271
8.8958 | 19067 | 420.05 | 61.4411
8.9062 | 26211 | 439.142 | 63.4723
8.9167 | 24096 | 445.193 | 63.0493
8.9271 | 23071 | 445.77 | 63.1374
8.9375 | 22388 | 443.7 | 62.7882
8.9479 | 17483 | 424.981 | 60.6968
8.9583 | 25814 | 438.815 | 62.1558
8.9688 | 23248 | 438.995 | 60.8936
8.9792 | 24098 | 440.224 | 59.4942
8.9896 | 22402 | 435.94 | 57.6492
9 | 19962 | 424.663 | 55.7787
9.0104 | 18363 | 408.694 | 54.052
9.0208 | 18618 | 398.5 | 53.4005
9.0312 | 19046 | 393.304 | 54.0072
9.0417 | 23433 | 403.839 | 55.8547
9.0521 | 22011 | 408.218 | 57.494
9.0625 | 23310 | 417.413 | 60.3042
9.0729 | 23158 | 425.681 | 63.6884
9.0833 | 15122 | 402.222 | 61.2692
9.0938 | 15319 | 383.34 | 59.1361
9.1042 | 15342 | 368.602 | 57.8633
9.1146 | 14751 | 351.82 | 54.5867
9.125 | 14287 | 339.78 | 54.1525
9.1354 | 12478 | 319.354 | 49.86
9.1458 | 12477 | 306.971 | 47.0735
9.1562 | 11347 | 288.387 | 42.9492
9.1667 | 11037 | 272.158 | 39.5317
9.1771 | 10473 | 258.031 | 37.3391
9.1875 | 10000 | 244.708 | 35.3368
9.1979 | 11258 | 236.118 | 32.9808
9.2083 | 10436 | 228.58 | 32.7738
9.2188 | 10976 | 223.715 | 32.7517
9.2292 | 11250 | 219.452 | 32.5681
9.2396 | 11740 | 217.583 | 32.4337
9.25 | 11562 | 214.543 | 32.1932
9.2604 | 12124 | 213.759 | 32.1206
9.2708 | 12578 | 214.146 | 32.0669
9.2812 | 11399 | 210.837 | 31.7729
9.2917 | 11448 | 208.333 | 31.3924
9.3021 | 12090 | 208.104 | 31.2848
9.3125 | 12429 | 209.075 | 31.3432
9.3229 | 11500 | 207.25 | 31.3021
9.3333 | 11717 | 206.549 | 31.5962
9.3438 | 11751 | 206.058 | 32.0029
9.3542 | 11489 | 205.392 | 32.3335
9.3646 | 12859 | 208.553 | 33.0545
9.375 | 12350 | 210.671 | 33.7289
9.3854 | 12194 | 215.612 | 36.7544
9.3958 | 15329 | 235.446 | 43.5039
9.4062 | 22901 | 274.793 | 51.3433
9.4167 | 23690 | 308.419 | 57.3952
9.4271 | 24749 | 348.238 | 65.8922
9.4375 | 27249 | 388.599 | 72.1988
9.4479 | 29504 | 430.668 | 78.0024
9.4583 | 31868 | 471.119 | 81.7277
9.4688 | 32126 | 501.093 | 82.8183
9.4792 | 31909 | 519.703 | 80.1568
9.4896 | 31927 | 531.491 | 75.6282
9.5 | 31719 | 540.931 | 74.0521
9.5104 | 30926 | 545.833 | 71.7672
9.5208 | 27039 | 534.318 | 67.4463
9.5312 | 25844 | 522.549 | 64.2129
9.5417 | 25174 | 510.637 | 61.7857
9.5521 | 24783 | 502.414 | 60.1625
9.5625 | 24444 | 495.288 | 59.0782
9.5729 | 22762 | 484.346 | 57.4214
9.5833 | 24940 | 484.59 | 57.265
9.5938 | 24113 | 481.797 | 57.1685
9.6042 | 23320 | 476.538 | 56.1816
9.6146 | 22247 | 467.756 | 55.3931
9.625 | 21875 | 456.89 | 53.5683
9.6354 | 21863 | 447.211 | 52.5854
9.6458 | 21236 | 438.046 | 51.9954
9.6562 | 21473 | 432.225 | 52.1679
9.6667 | 20822 | 426.133 | 52.2435
9.6771 | 20463 | 420.443 | 51.7378
9.6875 | 20034 | 415.884 | 51.8146
9.6979 | 19328 | 411.428 | 52.5268
9.7083 | 18928 | 403.512 | 51.963
9.7188 | 18510 | 394.292 | 50.7516
9.7292 | 18319 | 383.021 | 48.8802
9.7396 | 18224 | 375.88 | 48.3042
9.75 | 19106 | 372.828 | 48.2561
9.7604 | 22491 | 383.189 | 50.1835
9.7708 | 21604 | 388.29 | 51.3022
9.7812 | 22228 | 395.84 | 52.8685
9.7917 | 21169 | 395.293 | 54.0189
9.8021 | 19849 | 391.428 | 53.5739
9.8125 | 17451 | 380.798 | 50.2297
9.8229 | 28091 | 516.241 | 49.4244
9.8333 | 38720 | 664.836 | 58.0238
9.8438 | 49360 | 800.222 | 67.1674
9.8542 | 60000 | 821.753 | 71.8455
9.8646 | 60000 | 749.712 | 67.0931
9.875 | 60000 | 717.766 | 62.6701
9.8854 | 60000 | 564.508 | 49.918
9.8958 | 60000 | 370.243 | 36.7836
9.9062 | 51083 | 363.237 | 41.474
9.9167 | 42165 | 342.228 | 41.0861
9.9271 | 33308 | 362.786 | 47.5165
9.9375 | 24339 | 455.04 | 63.7376
9.9479 | 21529 | 447.472 | 62.5471
9.9583 | 26978 | 460.136 | 63.5921
9.9688 | 25693 | 464.394 | 62.75
9.9792 | 24779 | 462.814 | 60.9137
9.9896 | 24086 | 460.173 | 59.3081
10 | 23308 | 455.71 | 58.0591
10.0104 | 21017 | 442.197 | 56.3229
10.0208 | 21014 | 433.315 | 55.7001
10.0312 | 19118 | 405.874 | 54.7171
10.0417 | 18847 | 406.265 | 55.3463
10.0521 | 18509 | 402.748 | 56.6966
10.0625 | 17886 | 400.461 | 58.5895
10.0729 | 17445 | 399.241 | 61.4038
10.0833 | 16858 | 392.979 | 60.998
10.0938 | 16116 | 396.435 | 59.9494
10.1042 | 16206 | 383.436 | 58.7755
10.1146 | 15965 | 368.325 | 55.624
10.125 | 14494 | 359.929 | 55.256
10.1354 | 13423 | 344.187 | 51.2798
10.1458 | 12660 | 333.85 | 48.5108
10.1562 | 12059 | 317.058 | 44.5218
10.1667 | 11453 | 300.831 | 41.0665
10.1771 | 12083 | 286.664 | 38.9763
10.1875 | 11554 | 272.898 | 36.9313
10.1979 | 11875 | 262.401 | 34.4051
10.2083 | 13101 | 254.173 | 34.3196
10.2188 | 12323 | 248.221 | 34.1344
10.2292 | 13271 | 246.103 | 34.1179
10.2396 | 13614 | 242.043 | 33.8593
10.25 | 13604 | 240.755 | 33.7205
10.2604 | 12382 | 240.733 | 33.5579
10.2708 | 12408 | 240.457 | 33.4419
10.2812 | 11767 | 236.243 | 33.1272
10.2917 | 12006 | 233.013 | 32.7228
10.3021 | 11805 | 228.517 | 32.3369
10.3125 | 11951 | 225.931 | 32.1978
10.3229 | 12317 | 223.087 | 32.186
10.3333 | 12825 | 221.208 | 32.4388
10.3438 | 12800 | 220.628 | 32.8367
10.3542 | 12600 | 221.957 | 33.2743
10.3646 | 13408 | 222.805 | 33.8454
10.375 | 13952 | 223.935 | 34.5353
10.3854 | 17235 | 230.837 | 37.8998
10.3958 | 17233 | 245.177 | 44.1624
10.4062 | 21804 | 265.157 | 50.7094
10.4167 | 25418 | 284.426 | 56.1452
10.4271 | 24776 | 322.005 | 64.3669
10.4375 | 26842 | 362.795 | 70.6257
10.4479 | 28519 | 395.642 | 75.7769
10.4583 | 30707 | 427.852 | 78.9244
10.4688 | 31000 | 456.023 | 79.8887
10.4792 | 31009 | 478.98 | 77.5178
10.4896 | 30713 | 495.397 | 73.2117
10.5 | 27093 | 509.635 | 71.3304
10.5104 | 25812 | 520.396 | 69.2902
10.5208 | 25808 | 516.967 | 66.1932
10.5312 | 24748 | 510.469 | 63.3038
10.5417 | 24677 | 503.054 | 61.2526
10.5521 | 21745 | 495.89 | 59.2389
10.5625 | 25678 | 493.274 | 59.1813
10.5729 | 25062 | 480.696 | 57.6096
10.5833 | 23552 | 487.077 | 57.1665
10.5938 | 22693 | 489.366 | 57.3571
10.6042 | 20001 | 485.226 | 56.1045
10.6146 | 18269 | 478.271 | 55.3135
10.625 | 24508 | 460.124 | 54.1848
10.6354 | 22354 | 437.134 | 52.0879
10.6458 | 20755 | 445.688 | 52.3514
10.6562 | 21824 | 442.89 | 52.8291
10.6667 | 17785 | 435.839 | 52.3181
10.6771 | 17047 | 434.983 | 52.0264
10.6875 | 18755 | 420.746 | 51.8984
10.6979 | 18708 | 407.608 | 52.2267
10.7083 | 19125 | 400.63 | 51.8299
10.7188 | 18535 | 392.776 | 50.6709
10.7292 | 18029 | 386.203 | 49.0176
10.7396 | 17772 | 380.609 | 48.5062
10.75 | 18093 | 374.177 | 48.2004
10.7604 | 18205 | 368.454 | 48.8008
10.7708 | 18209 | 367.506 | 49.6981
10.7812 | 18193 | 368.129 | 50.7872
10.7917 | 22437 | 365.306 | 52.4768
10.8021 | 21842 | 363.401 | 52.2468
10.8125 | 21390 | 376.101 | 50.4751
10.8229 | 21824 | 387.915 | 53.0273
10.8333 | 18403 | 393.24 | 52.936
10.8438 | 20104 | 400.066 | 54.0822
10.8542 | 23390 | 396.287 | 56.285
10.8646 | 21850 | 401.222 | 58.1621
10.875 | 22120 | 415.236 | 59.6069
10.8854 | 21151 | 421.553 | 61.2809
10.8958 | 18582 | 428.336 | 61.8336
10.9062 | 25345 | 429.74 | 62.7955
10.9167 | 23343 | 421.569 | 61.5765
10.9271 | 22372 | 438.576 | 62.6217
10.9375 | 21725 | 442.859 | 62.6414
10.9479 | 17083 | 442.424 | 61.5956
10.9583 | 24968 | 439.346 | 62.0608
10.9688 | 22540 | 420.363 | 59.7208
10.9792 | 23343 | 432.824 | 58.9531
10.9896 | 21738 | 432.716 | 57.3653
11 | 19429 | 435.736 | 56.3185
11.0104 | 17915 | 430.006 | 55.1639
11.0208 | 18156 | 418.73 | 54.4548
11.0312 | 18561 | 406.677 | 54.6829
11.0417 | 22713 | 398.89 | 55.4701
11.0521 | 21366 | 396.066 | 56.714
11.0625 | 22596 | 409.429 | 59.7443
11.0729 | 22452 | 415.684 | 63.0138
11.0833 | 14847 | 421.931 | 62.2919
11.0938 | 15033 | 423.196 | 61.2462
11.1042 | 15055 | 397.158 | 59.3666
11.1146 | 14496 | 376.33 | 55.8711
11.125 | 14056 | 363.267 | 55.3815
11.1354 | 12345 | 342.654 | 51.0726
11.1458 | 12344 | 331.926 | 48.374
11.1562 | 11274 | 315.622 | 44.3631
11.1667 | 10981 | 298.828 | 40.9146
11.1771 | 10448 | 282.636 | 38.6115
11.1875 | 10000 | 268.347 | 36.5564
11.1979 | 11190 | 253.645 | 33.8895
11.2083 | 10412 | 242.497 | 33.4927
11.2188 | 10923 | 236.877 | 33.4326
11.2292 | 11182 | 228.643 | 33.0427
11.2396 | 11646 | 223.762 | 32.7509
11.25 | 11478 | 219.443 | 32.4438
11.2604 | 12009 | 217.245 | 32.2963
11.2708 | 12439 | 214.596 | 32.0816
11.2812 | 11323 | 213.56 | 31.9103
11.2917 | 11370 | 213.733 | 31.6695
11.3021 | 11977 | 210.569 | 31.4071
11.3125 | 12298 | 208.554 | 31.3075
11.3229 | 11419 | 208.637 | 31.3696
11.3333 | 11624 | 209.623 | 31.7514
11.3438 | 11656 | 207.83 | 32.0899
11.3542 | 11409 | 207.518 | 32.4396
11.3646 | 12704 | 207.316 | 32.9798
11.375 | 12223 | 207.473 | 33.5528
11.3854 | 12076 | 214.902 | 36.7098
11.3958 | 15040 | 226.609 | 43.0091
11.4062 | 22202 | 238.297 | 49.2054
11.4167 | 22948 | 255.559 | 54.2937
11.4271 | 23950 | 298.211 | 62.9167
11.4375 | 26314 | 334.153 | 68.8837
11.4479 | 28447 | 368.497 | 74.1429
11.4583 | 30682 | 402.767 | 77.3937
11.4688 | 30926 | 434.341 | 78.5557
11.4792 | 30720 | 463.112 | 76.5074
11.4896 | 30737 | 484.454 | 72.5488
11.5 | 30540 | 502.265 | 71.4789
11.5104 | 29790 | 517.266 | 69.8204
11.5208 | 26113 | 527.245 | 66.8538
11.5312 | 24983 | 533.06 | 64.6646
11.5417 | 24349 | 523.24 | 62.3652
11.5521 | 23979 | 514.893 | 60.7388
11.5625 | 23658 | 507.141 | 59.6219
11.5729 | 22068 | 500.749 | 58.2357
11.5833 | 24127 | 495.185 | 57.7373
11.5938 | 23345 | 485.528 | 57.2508
11.6042 | 22595 | 486.089 | 56.6052
11.6146 | 21580 | 481.879 | 56.0845
11.625 | 21228 | 472.845 | 54.3669
11.6354 | 21217 | 460.952 | 53.2603
11.6458 | 20623 | 451.353 | 52.6496
11.6562 | 20848 | 444.386 | 52.7581
11.6667 | 20232 | 437.551 | 52.7958
11.6771 | 19893 | 433.371 | 52.3776
11.6875 | 19487 | 429.056 | 52.4707
11.6979 | 18819 | 425.985 | 53.2633
11.7083 | 18441 | 418.967 | 52.7516
11.7188 | 18045 | 409.461 | 51.5264
11.7292 | 17864 | 397.339 | 49.6095
11.7396 | 17775 | 388.533 | 48.9431
11.75 | 18608 | 380.723 | 48.63
11.7604 | 21808 | 376.141 | 49.6919
11.7708 | 20969 | 375.871 | 50.5151
11.7812 | 21559 | 387.657 | 52.3127
11.7917 | 20558 | 390.1 | 53.6431
11.8021 | 19310 | 394.71 | 53.6844
11.8125 | 17043 | 394.839 | 50.9456
11.8229 | 17878 | 395.529 | 52.9297
11.8333 | 21360 | 385.882 | 52.9126
11.8438 | 22636 | 382.453 | 53.4169
11.8542 | 22542 | 394.058 | 56.0451
11.8646 | 24225 | 407.791 | 58.859
11.875 | 20907 | 416.799 | 59.5274
11.8854 | 18809 | 431.235 | 61.4905
11.8958 | 20576 | 431.369 | 62.2877
11.9062 | 25680 | 424.259 | 62.5217
11.9167 | 23444 | 425.189 | 61.7991
11.9271 | 32755 | 380.088 | 48.1048
11.9375 | 42075 | 347.285 | 40.889
11.9479 | 51395 | 314.171 | 33.4217
11.9583 | 60000 | 295.519 | 33.4412
11.9688 | 60000 | 273.306 | 30.7594
11.9792 | 60000 | 250.918 | 27.8938
11.9896 | 60000 | 229.414 | 25.3988
12 | 60000 | 208.028 | 23.1072
12.0104 | 60000 | 179.312 | 19.7284
12.0208 | 60000 | 172.773 | 19.2284
12.0312 | 60000 | 144.795 | 16.8536
12.0417 | 60000 | 141.643 | 16.7209
12.0521 | 60000 | 138.77 | 16.8449
12.0625 | 60000 | 134.259 | 16.8324
12.0729 | 60000 | 134.731 | 17.4117
12.0833 | 60000 | 128.465 | 16.6733
12.0938 | 54889 | 129.266 | 16.8909
12.1042 | 54086 | 128.329 | 16.9364
12.1146 | 52970 | 125.449 | 16.1681
12.125 | 50691 | 117.6 | 15.2465
12.1354 | 48790 | 108.875 | 13.5666
12.1458 | 47180 | 103.989 | 12.5137
12.1562 | 45723 | 98.5613 | 11.2912
12.1667 | 44262 | 93.3916 | 10.2263
12.1771 | 43968 | 94.4544 | 10.3224
12.1875 | 42579 | 90.975 | 9.7125
12.1979 | 41993 | 90.9585 | 9.4223
12.2083 | 42262 | 96.0947 | 10.3634
12.2188 | 40639 | 93.6188 | 10.1419
12.2292 | 40646 | 97.88 | 10.8921
12.2396 | 40081 | 100.644 | 11.3095
12.25 | 39182 | 101.983 | 11.5242
12.2604 | 37139 | 98.0979 | 10.9912
12.2708 | 36275 | 98.8404 | 11.1879
12.2812 | 34780 | 96.6972 | 10.9812
12.2917 | 34117 | 98.2376 | 11.2726
12.3021 | 33039 | 98.2209 | 11.3433
12.3125 | 32287 | 99.9367 | 11.7062
12.3229 | 31744 | 102.977 | 12.2941
12.3333 | 31335 | 107.221 | 13.1064
12.3438 | 30422 | 109.621 | 13.6647
12.3542 | 29345 | 111.439 | 14.1176
12.3646 | 29219 | 117.993 | 15.3468
12.375 | 28843 | 124.862 | 16.5698
12.3854 | 31055 | 145.168 | 20.8721
12.3958 | 30164 | 160.745 | 25.2089
12.4062 | 33592 | 199.098 | 33.0858
12.4167 | 36115 | 238.827 | 40.2176
12.4271 | 34619 | 268.983 | 46.6232
12.4375 | 35682 | 308.551 | 53.3734
12.4479 | 36376 | 349.162 | 59.7225
12.4583 | 37553 | 389.638 | 64.8082
12.4688 | 36940 | 419.245 | 67.1168
12.4792 | 36059 | 441.304 | 66.4035
12.4896 | 34891 | 457.49 | 63.8683
12.5 | 30584 | 457.88 | 61.879
12.5104 | 28485 | 461.67 | 60.6473
12.5208 | 27592 | 467.323 | 59.4994
12.5312 | 25702 | 470.774 | 58.4114
12.5417 | 24746 | 479.991 | 58.5579
12.5521 | 21088 | 482.346 | 58.3551
12.5625 | 24802 | 487.172 | 58.6696
12.5729 | 24220 | 488.185 | 57.8984
12.5833 | 22794 | 483.723 | 56.8411
12.5938 | 21983 | 478.182 | 56.5947
12.6042 | 19441 | 463.805 | 54.811
12.6146 | 17806 | 443.922 | 53.3414
12.625 | 23695 | 451.218 | 53.5371
12.6354 | 21662 | 445.711 | 52.4679
12.6458 | 20152 | 436.331 | 51.7294
12.6562 | 21161 | 433.833 | 52.2108
12.6667 | 17348 | 417.816 | 51.2606
12.6771 | 16651 | 402.052 | 50.1675
12.6875 | 18264 | 397.534 | 50.542
12.6979 | 18220 | 394.731 | 51.4461
12.7083 | 18613 | 392.367 | 51.3012
12.7188 | 18056 | 386.359 | 50.2521
12.7292 | 17578 | 376.468 | 48.4219
12.7396 | 17335 | 368.187 | 47.7669
12.75 | 17638 | 364.455 | 47.6067
12.7604 | 17744 | 363.648 | 48.4781
12.7708 | 17747 | 363.481 | 49.4189
12.7812 | 17733 | 364.512 | 50.531
12.7917 | 21738 | 376.541 | 53.0299
12.8021 | 21176 | 383.808 | 53.321
12.8125 | 20749 | 388.158 | 51.0735
12.8229 | 21158 | 398.101 | 53.5167
12.8333 | 17930 | 391.676 | 52.7867
12.8438 | 19535 | 394.139 | 53.6737
12.8542 | 22636 | 409.78 | 56.9579
12.8646 | 21182 | 417.213 | 58.9788
12.875 | 21436 | 423.276 | 59.9684
12.8854 | 20522 | 426.09 | 61.4483
12.8958 | 18098 | 420.05 | 61.3071
12.9062 | 24479 | 439.141 | 63.2187
12.9167 | 22590 | 445.192 | 62.8249
12.9271 | 21673 | 445.769 | 62.9284
12.9375 | 21063 | 443.699 | 62.5904
12.9479 | 16683 | 424.981 | 60.5834
12.9583 | 24122 | 438.815 | 61.9038
12.9688 | 21831 | 438.995 | 60.6809
12.9792 | 22589 | 440.223 | 59.2643
12.9896 | 21074 | 435.94 | 57.4481
13 | 18895 | 424.663 | 55.6216
13.0104 | 16990 | 338.279 | 50.0027
13.0208 | 16990 | 331.66 | 49.5169
13.0312 | 15964 | 328.748 | 50.085
13.0417 | 15806 | 334.966 | 51.0517
13.0521 | 15610 | 338.529 | 52.8192
13.0625 | 15247 | 345.206 | 55.2488
13.0729 | 14989 | 351.794 | 58.521
13.0833 | 14647 | 338.589 | 57.789
13.0938 | 14212 | 326.681 | 55.9643
13.1042 | 14266 | 317.322 | 54.9879
13.1146 | 14126 | 305.764 | 52.0521
13.125 | 13264 | 298.654 | 51.8563
13.1354 | 12636 | 283.361 | 47.9771
13.1458 | 12189 | 276.608 | 45.4481
13.1562 | 11836 | 264.125 | 41.7233
13.1667 | 11481 | 253.269 | 38.5836
13.1771 | 11851 | 244.348 | 36.7356
13.1875 | 11540 | 235.974 | 34.9994
13.1979 | 11729 | 229.963 | 32.6937
13.2083 | 12450 | 225.821 | 32.7718
13.2188 | 11994 | 223.206 | 32.795
13.2292 | 12552 | 220.635 | 32.7178
13.2396 | 12755 | 219.725 | 32.6139
13.25 | 12749 | 217.828 | 32.4436
13.2604 | 12030 | 217.397 | 32.3056
13.2708 | 12046 | 217.63 | 32.2154
13.2812 | 11668 | 215.643 | 32.0415
13.2917 | 11810 | 214.125 | 31.7184
13.3021 | 11692 | 213.966 | 31.567
13.3125 | 11778 | 214.649 | 31.5946
13.3229 | 11994 | 213.705 | 31.6714
13.3333 | 12294 | 213.435 | 31.9938
13.3438 | 12280 | 213.269 | 32.4144
13.3542 | 12162 | 213.185 | 32.7836
13.3646 | 12640 | 215.238 | 33.394
13.375 | 12962 | 217.104 | 34.107
13.3854 | 14903 | 221.997 | 37.2646
13.3958 | 14903 | 238.126 | 43.6202
13.4062 | 17608 | 265.681 | 50.4291
13.4167 | 19748 | 288.665 | 55.9374
13.4271 | 19370 | 317.918 | 63.6594
13.4375 | 20596 | 345.785 | 69.0289
13.4479 | 21592 | 374.034 | 73.7686
13.4583 | 22891 | 399.399 | 76.3141
13.4688 | 23068 | 416.261 | 76.5074
13.4792 | 23077 | 424.12 | 73.1621
13.4896 | 22905 | 426.867 | 68.0027
13.5 | 20762 | 429.12 | 65.69
13.5104 | 20005 | 429.274 | 63.1281
13.5208 | 20005 | 419.678 | 59.6764
13.5312 | 19379 | 410.599 | 56.7519
13.5417 | 19339 | 401.486 | 54.6183
13.5521 | 17601 | 395.896 | 52.9963
13.5625 | 19939 | 391.3 | 52.4407
13.5729 | 19576 | 384.906 | 51.3068
13.5833 | 18681 | 385.221 | 50.6586
13.5938 | 18173 | 384.074 | 50.7415
13.6042 | 16574 | 381.34 | 49.8413
13.6146 | 15545 | 376.127 | 49.3229
13.625 | 19259 | 368.552 | 48.2167
13.6354 | 17980 | 361.503 | 47.2343
13.6458 | 17030 | 355.44 | 46.813
13.6562 | 17669 | 351.76 | 47.151
13.6667 | 15264 | 348.452 | 47.2095
13.6771 | 14826 | 345.533 | 46.8725
13.6875 | 15846 | 343.854 | 47.2991
13.6979 | 15819 | 342.747 | 48.3051
13.7083 | 16069 | 338.081 | 48.0124
13.7188 | 15719 | 332.083 | 47.0047
13.7292 | 15418 | 323.696 | 45.2916
13.7396 | 15266 | 319.073 | 44.8559
13.75 | 15459 | 316.907 | 44.765
13.7604 | 15528 | 323.517 | 46.0335
13.7708 | 15531 | 327.252 | 47.1872
13.7812 | 15524 | 332.832 | 48.5481
13.7917 | 18062 | 332.175 | 50.1099
13.8021 | 17708 | 329.891 | 49.8972
13.8125 | 17440 | 323.65 | 47.0884
13.8229 | 17701 | 325.33 | 49.0407
13.8333 | 15656 | 330.898 | 49.1949
13.8438 | 16676 | 338.019 | 50.2292
13.8542 | 18646 | 345.666 | 52.8478
13.8646 | 17726 | 356.327 | 55.1411
13.875 | 17889 | 356.764 | 55.7966
13.8854 | 17311 | 354.572 | 57.0663
13.8958 | 15773 | 357.441 | 57.5925
13.9062 | 19830 | 369.355 | 58.6288
13.9167 | 18631 | 372.87 | 58.2231
13.9271 | 18051 | 374.18 | 58.4337
13.9375 | 17665 | 375.615 | 58.3357
13.9479 | 14880 | 370.46 | 57.3953
13.9583 | 19617 | 376.895 | 57.77
13.9688 | 18161 | 378.534 | 56.7888
13.9792 | 18646 | 376.09 | 55.1057
13.9896 | 17683 | 373.579 | 53.5016
14 | 16297 | 370.197 | 52.2747

## Model
Model overview
Name: | Sumo1
Settings
Key parameters
Symbol | Name | Value | Unit | Comment
iCV,XB | COD of biodegradable substrate in volatile solids | 1.8 | g COD.g VSS-1
iCV,XU | COD of particulate unbiodegradable organics in volatile solids | 1.3 | g COD.g VSS-1
iCV,BIO | COD of biomass in volatile solids | 1.42 | g COD.g VSS-1
iCV,XE | COD of endogenous products in volatile solids | 1.42 | g COD.g VSS-1
μNITO | Maximum specific growth rate of NITOs | 0.9 | 1/d
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.25 | g O2/m3
KNHx,NITO,AS | Half-saturation of NHx for NITOs (AS) | 0.7 | g N/m3
μOHO | Maximum specific growth rate of OHOs | 4 | 1/d
KSB,AS | Half-saturation of readily biodegradable substrate for OHOs (AS) | 5 | g COD/m3
KO2,OHO,AS | Half-saturation of O2 for OHOs (AS) | 0.05 | g O2/m3
μPAO | Maximum specific growth rate of PAOs | 1 | 1/d
μGAO | Maximum specific growth rate of GAOs | 0.55 | 1/d
KPO4,PAO,AS | Half-saturation of PO4 for PAOs (AS) | 0.5 | g P/m3
qHYD | Rate of hydrolysis | 2 | 1/d
Ordinary heterotrophic organism kinetics (OHO)
Symbol | Name | Value | Unit | Comment
μOHO | Maximum specific growth rate of OHOs | 4 | 1/d
μFERM,OHO | Fermentation growth rate of OHOs | 0.3 | 1/d
bOHO | Decay rate of OHOs | 0.62 | 1/d
ηOHO,anox | Reduction factor for anoxic growth of OHOs | 0.6
KSB,AS | Half-saturation of readily biodegradable substrate for OHOs (AS) | 5 | g COD/m3
KO2,OHO,AS | Half-saturation of O2 for OHOs (AS) | 0.05 | g O2/m3
KVFA,AS | Half-saturation of VFA for OHOs (AS) | 0.5 | g COD/m3
KMEOL,OHO,AS | Half-saturation of methanol for OHOs (AS) | 0.1 | g COD/m3
KNOx,OHO,AS | Half-saturation of NOx for OHOs (AS) | 0.03 | g N/m3
KVFA,FERM,AS | Half-saturation of VFA in fermentation of OHOs (AS) | 50 | g COD/m3
KSB,ana,AS | Half-saturation of readily biodegradable substrate in fermentation by OHOs (AS) | 350 | g COD/m3
Anoxic methanol utilizer kinetics (MEOLO)
Symbol | Name | Value | Unit | Comment
μMEOLO | Maximum specific growth rate of MEOLOs | 1.3 | 1/d
bMEOLO | Decay rate of MEOLOs | 0.05 | 1/d
qMEOL | Rate of methanol degradation by MEOLOs under anaerobic conditions | 10 | 1/d | To clean up any remaining methanol in digesters without having to ferment mechanistically
KMEOL,AS | Half-saturation of methanol for MEOLOs (AS) | 0.5 | g COD/m3
KiO2,MEOLO,AS | Half-inhibition of O2 for MEOLOs (AS) | 0.05 | g O2/m3
KNOx,MEOLO,AS | Half-saturation of NOx for MEOLOs (AS) | 0.03 | g N/m3
Phosphorus accumulating organism kinetics (PAO)
Symbol | Name | Value | Unit | Comment
μPAO | Maximum specific growth rate of PAOs | 1 | 1/d
μFERM,PAO | Fermentation growth rate of PAOs | 0.45 | 1/d
μPAO,lim | Maximum specific growth rate of PAOs under P limited | 0.49 | 1/d
bPAO | Decay rate of PAOs | 0.05 | 1/d | (0.15 for Lopez et al. 2006; Hao et al., 2010)
bPHA | Rate of PAOs maintenance on PHA | 0.05 | 1/d
bPP,ana | Rate of PAOs maintenance under anaerobic conditions (PP cleavage) | 0.005 | 1/d
qPAO,PHA | Rate of VFA storage into PHA for PAOs | 4 | 1/d
ηPAO,anox | Reduction factor for anoxic growth of PAOs | 0.66
ηbPAO,anox | Reduction factor for anoxic decay of PAOs | 0.5
ηbPAO,ana | Reduction factor for anaerobic decay of PAOs | 0.25
ηbPHA,anox | Reduction factor for anoxic maintenance of PAOs on PHA | 0.66
ηbPP,aer | Reduction factor for aerobic maintenance of PAOs on PP | 0.25
ηbPP,anox | Reduction factor for anoxic maintenance of PAOs on PP | 0.5
KPO4,PAO,AS | Half-saturation of PO4 for PAOs (AS) | 0.5 | g P/m3
KPHA | Half-saturation of PHA for PAOs | 0.1 | g COD/m3
KO2,PAO,AS | Half-saturation of O2 for PAOs (AS) | 0.05 | g O2/m3
KNOx,PAO,AS | Half-saturation of NOx for PAOs (AS) | 0.03 | g N/m3
KVFA,PAO,AS | Half-saturation of VFA storage for PAOs (AS) | 5 | g COD/m3
KPP | Half-saturation of PP for PAOs | 0.01 | g P/m3
KiPP,PAO,max | Half-inhibition of maximum PP content of PAOs | 99 | g P.g COD-1
KiPHA,PAO,max | Half-inhibition of maximum PHA content of PAOs | 0.6 | g COD.g COD-1
KMg,PAO,AS | Half-saturation of Mg (counter-ion in PP storage) for PAOs (AS) | 0.001 | g Mg/m3
KK,PAO,AS | Half-saturation of K (counter-ion in PP storage) for PAOs (AS) | 0.001 | g K/m3
KCa,PAO,AS | Half-saturation of Ca (counter-ion in PP storage) for PAOs (AS) | 0.001 | g Ca/m3
KPP,lim | Half-saturation of PP (nutrient) for PAOs under PO4 limitation (AS) | 0.002 | g P/m3
KiPO4,lim,AS | Half-inhibition of PO4 for PAOs under PO4 limitation (AS) | 0.005 | g P/m3
LogsatORP,PAO,Half | Logistic half-saturation of ORP switching in fermentation of PAO | -100 | mV
LogsatORP,PAO,Slope | Logistic slope of ORP switching in fermentation of PAO | 0.1 | mV-1
Glycogen accumulating organism kinetics (GAO)
Symbol | Name | Value | Unit | Comment
μGAO | Maximum specific growth rate of GAOs | 0.55 | 1/d
bGAO | Decay rate of GAOs | 0.05 | 1/d | (0.13 for Hao et al., 2010)
bGLY | Rate of GAOs maintenance on glycogen | 0.1 | 1/d
qGAO,GLY | Rate of VFA storage into glycogen for GAOs | 4 | 1/d
ηGAO,anox | Reduction factor for anoxic growth of GAOs | 0.33
ηbGAO,anox | Reduction factor for anoxic decay of GAOs | 0.5
ηbGAO,ana | Reduction factor for anaerobic decay of GAOs | 0.25
ηbGLY,anox | Reduction factor for anoxic maintenance of GAOs on glycogen | 0.33
ηbGLY,ana | Reduction factor for anaerobic maintenance of GAOs on glycogen | 0.1
KGLY | Half-saturation of glycogen for GAOs (AS) | 0.05 | g COD/m3
KO2,GAO,AS | Half-saturation of O2 for GAOs (AS) | 0.2 | g O2/m3
KNOx,GAO,AS | Half-saturation of NOx for GAOs (AS) | 0.03 | g N/m3
KiGLY,GAO,max | Half-inhibition of maximum glycogen content of GAOs (AS) | 0.5 | g COD.g COD-1
KVFA,GAO,AS | Half-saturation of VFA storage for GAOs (AS) | 5 | g COD/m3
LogsatORP,GAO,Half | Logistic half-saturation of ORP switching of GAOs | -100 | mV
LogsatORP,GAO,Slope | Logistic slope of ORP switching of GAOs | 0.1 | mV-1
Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
μNITO | Maximum specific growth rate of NITOs | 0.9 | 1/d
bNITO | Decay rate of NITOs | 0.17 | 1/d
KNHx,NITO,AS | Half-saturation of NHx for NITOs (AS) | 0.7 | g N/m3
KCO2,NITO,AS | Half-saturation of CO2 for NITOs (AS) | 12 | g TIC/m3 | if pH is not calculated
KCO2,NITO,sidestream | Half-saturation of CO2 for NITOs (Sidestream) | 48 | g TIC/m3 | if pH is not calculated
KCO2,NITO,pH,AS | Half-saturation of bicarbonate for NITOs (AS) | 1 | mmol [HCO3-]/L | if pH is calculated
KCO2,NITO,pH,sidestream | Half-saturation of bicarbonate for NITOs (Sidestream) | 4 | mmol [HCO3-]/L | if pH is calculated
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.25 | g O2/m3
KO2,NITO,sidestream | Half-saturation of O2 for NITOs (Sidestream) | 0.5 | g O2/m3
KNOx,NITO,AS | Half-saturation of NOx for NITOs (AS) | 0.03 | g N/m3
KiNH3,NITO,pH,AS | Half-inhibition of NH3 for NITOs (AS) | 9999 | mol [NH3].L-1 | if pH is calculated
Acidoclastic methanogen kinetics (AMETO)
Symbol | Name | Value | Unit | Comment
μAMETO | Maximum specific growth rate of AMETO | 0.3 | 1/d
bAMETO | Decay rate of AMETOs | 0.03 | 1/d
KVFA,AMETO,AS | Half-saturation of VFA for AMETOs (AS) | 400 | g COD/m3 | Non-pH
KiVFA,AMETO,AS | Haldane inhibition of VFA for AMETOs (AS) | 99999 | g COD/m3 | Non-pH
KiO2,AMETO,AS | Half-inhibition of O2 for AMETOs (AS) | 0.05 | g O2/m3
KNOx,AMETO,AS | Half-saturation of NOx for AMETOs (AS) | 0.05 | g N/m3
pHlow,AMETO | pH inhibition low value for AMETOs | 4.5 | pHunit
pHhigh,AMETO | pH inhibition high value for AMETOs | 9.5 | pHunit
Hydrogenotrophic methanogen kinetics (HMETO)
Symbol | Name | Value | Unit | Comment
μHMETO | Maximum specific growth rate of HMETO | 1.3 | 1/d
bHMETO | Decay rate of HMETOs | 0.13 | 1/d
KH2,HMETO,AS | Half-saturation of H2 for HMETOs (AS) | 0.1 | g COD/m3
KiO2,HMETO,AS | Half-inhibition of O2 for HMETOs (AS) | 0.05 | g O2/m3
KNOx,HMETO,AS | Half-saturation of NOx for HMETOs (AS) | 0.05 | g N/m3
pHlow,HMETO | pH inhibition low value for HMETOs | 4.5 | pHunit
pHhigh,HMETO | pH inhibition high value for HMETOs | 9.5 | pHunit
Precipitation kinetics
Symbol | Name | Value | Unit | Comment
qCaCO3,PREC | Rate of CaCO3 precipitation | 0.1 | g.m-3.d-1
qCaCO3,DISS | Rate of CaCO3 dissolution | 0.01 | g.m-3.d-1
qSTR,PREC | Rate of struvite precipitation | 10 | g.m-3.d-1
qSTR,DISS | Rate of struvite dissolution | 1 | g.m-3.d-1
qACP,PREC | Rate of ACP precipitation | 0.5 | g.m-3.d-1
qACP,DISS | Rate of ACP dissolution | 0.05 | g.m-3.d-1
qVivi,PREC | Rate of vivianite precipitation | 0.01 | g.m-3.d-1
qVivi,DISS | Rate of vivianite dissolution | 0.001 | g.m-3.d-1
KSTR,DISS | Half-saturation of struvite redissolution | 0.01 | g TSS/m3
KACP,DISS | Half-saturation of ACP redissolution | 0.01 | g TSS/m3
KCaCO3,DISS | Half-saturation of CaCO3 redissolution | 0.01 | g TSS/m3
KVivi,DISS | Half-saturation of vivianite redissolution | 0.01 | g TSS/m3
HFO kinetics
Symbol | Name | Value | Unit | Comment
qHFOH,AGING | Rate of XHFO,H aging | 250 | 1/d
qHFOL,AGING | Rate of XHFO,L aging | 1 | 1/d
qP,COPREC | Rate of P binding and coprecipitation on XHFO,H | 150 | 1/d
qP,BIND | Rate of P binding on XHFO,L | 1 | 1/d
qHFOH,DESORP | Rate of XHFO,H,P desorption | 100 | 1/d
qHFOL,DESORP | Rate of XHFO,L,P desorption | 10 | 1/d
qHFO,DISS | Rate of XHFO,H,P,old and XHFO,L,P,old redissolution | 100 | 1/d
qHFO,RED | Rate of HFO reduction with organics | 2 | 1/d
LogsatORP,HFO,Half | Logistic half-saturation of ORP switching in HFO reduction | -100 | mV
LogsatORP,HFO,Slope | Logistic slope of ORP switching in HFO reduction | 0.1
qFe2,OX | Rate of Fe2 oxidation | 1 | 1/d
KiP,DISS | Half-inhibition of PO4 in HFO redissolution | 0.01 | g P/m3
KiP,DESORP | Half-inhibition of PO4 in HFO desorption | 0.1 | g P/m3
KP,BIND | Half-saturation of PO4 in binding on HFO | 0.1 | g P/m3
Aluminium phosphate precipitation kinetics
Symbol | Name | Value | Unit | Comment
qAlOH,PREC | Rate of AlOH precipitation | 5 | 1/d
qAlOH,DISSOL | Rate of AlOH dissolution | 0.6 | 1/d
Common switches
Symbol | Name | Value | Unit | Comment
KNHx,BIO,AS | Half-saturation of NHx as nutrient for biomasses (AS) | 0.005 | g N/m3
KPO4,BIO,AS | Half-saturation of PO4 as nutrient for biomasses (AS) | 0.002 | g P/m3
KCO2,BIO,AS | Half-saturation of CO2 for biomasses (except NITOs) | 1.2 | g TIC/m3
KCAT,AS | Half-saturation of strong cations (as Na+) | 0.1 | g Na/m3
KAN,AS | Half-saturation of strong anions (as Cl-) | 0.1 | g Cl/m3
ηb,anox | Reduction factor for anoxic decay | 0.5
ηb,ana | Reduction factor for anaerobic decay | 0.25
mtox,anox | Toxicity factor of anaerobes under anoxic conditions | 5
mtox,aer | Toxicity factor of anaerobes under aerobic conditions | 10
mtox,ana,max | Toxicity factor of aerobes under anaerobic conditions (maximum) | 10
pHlow | pH inhibition low value | 3 | pHunit
pHhigh | pH inhibition high value | 11 | pHunit
Conversion kinetics
Symbol | Name | Value | Unit | Comment
qHYD | Rate of hydrolysis | 2 | 1/d
ηHYD,anox | Reduction factor for anoxic hydrolysis | 0.5
ηHYD,ana | Reduction factor for anaerobic hydrolysis | 0.5
qFLOC | Rate of flocculation | 50 | 1/d
KFLOC,AS | Half-saturation of colloids in flocculation (AS) | 0.001 | g COD.g COD-1
KHYD,AS | Half-saturation of particulates in hydrolysis (AS) | 0.05 | g COD.g COD-1
qAMMON | Rate of ammonification | 0.05 | 1/d
qSPB | Rate of soluble biodegradable organic P conversion | 0.5 | 1/d
qXE | Rate of endogenous decay products conversion | 0.007 | 1/d
qASSIM | Rate of assimilative nutrient production | 1 | 1/d
KiNHx,ASSIM,AS | Half-inhibition of NHx in NOx assimilative reduction | 0.0005 | g N/m3
KNOx,ASSIM,AS | Half-saturation of NOx in NOx assimilative reduction (AS) | 0.001 | g N/m3
Parameters for half saturation coefficients in biofilms
Symbol | Name | Value | Unit | Comment
fKS,biofilm | Diffusion factor for half-saturation coefficients | 0.1
Temperature dependency
Symbol | Name | Value | Unit | Comment
θμ,OHO | Arrhenius coefficient for OHO growth | 1.04
θFERM,OHO | Arrhenius coefficient for fermentation (OHO) | 1.04
θb,OHO | Arrhenius coefficient for OHO decay | 1.03
θμ,MEOLO | Arrhenius coefficient for MEOLO growth | 1.06
θb,MEOLO | Arrhenius coefficient for MEOLO decay | 1.03
θμ,PAO | Arrhenius coefficient for PAO growth | 1.04
θμ,PAO,lim | Arrhenius coefficient for PAO growth (P limited) | 1.04
θFERM,PAO | Arrhenius coefficient for fermentation (PAO) | 1.04
θq,PAO,PHA | Arrhenius coefficient for PHA storage | 1.04
θb,PAO | Arrhenius coefficient for PAO decay | 1.03
θb,PHA | Arrhenius coefficient for PHA storage use for maintenance | 1.064 |  | Lopez Vazquez et al., 2009
θb,PP,ana | Arrhenius coefficient for anaerobic PP storage | 1.03
θμ,GAO | Arrhenius coefficient for GAO growth | 1.072
θq,GAO,GLY | Arrhenius coefficient for GLY storage | 1.04
θb,GAO | Arrhenius coefficient for GAO decay | 1.03
θb,GLY | Arrhenius coefficient for GLY storage use for maintenance | 1.054 |  | Lopez Vazquez et al., 2009
θμ,NITO | Arrhenius coefficient for NITO growth | 1.072
θb,NITO | Arrhenius coefficient for NITO decay | 1.03
θμ,AMETO | Arrhenius coefficient for AMETO growth | 1.03
θb,AMETO | Arrhenius coefficient for AMETO decay | 1.03
θμ,HMETO | Arrhenius coefficient for HMETO growth | 1.03
θb,HMETO | Arrhenius coefficient for HMETO decay | 1.03
θq,FLOC | Arrhenius coefficient for flocculation | 1.03
θq,HYD | Arrhenius coefficient for hydrolysis | 1.03
θq,AMMON | Arrhenius coefficient for ammonification | 1.03
θq,SPB | Arrhenius coefficient for PO4 conversion | 1.03
θq,XE | Arrhenius coefficient endogenous residual conversion | 1.03
θq,ASSIM | Arrhenius coefficient assimilative kinetics | 1.03
θq,Fe2,OX | Arrhenius coefficient for ferrous iron oxidation kinetics | 1.04
θq,HFO,RED | Arrhenius coefficient for ferric iron reduction kinetics | 1.04
Tbase | Arrhenius base temperature | 20 | Co
Stoichiometric yields
Symbol | Name | Value | Unit | Comment
YOHO,VFA,ox | Yield of OHOs on VFA under aerobic conditions | 0.6 | g XOHO.g SVFA-1
YOHO,VFA,anox | Yield of OHOs on VFA under anoxic conditions | 0.45 | g XOHO.g SVFA-1
YOHO,SB,ox | Yield of OHOs on readily biodegradable substrate under aerobic conditions | 0.67 | g XOHO.g SB-1
YOHO,SB,anox | Yield of OHOs on readily biodegradable substrate under anoxic conditions | 0.54 | g XOHO.g SB-1
YOHO,SB,ana | Yield of OHOs on readily biodegradable substrate under anaerobic conditions | 0.1 | g XOHO.g SB-1
YOHO,H2,ana,high | Yield of H2 production in fermentation with high VFA concentration (OHO) | 0.35 | g SH2.g SB-1
YOHO,H2,ana,low | Yield of H2 production in fermentation with low VFA concentration (OHO) | 0.1 | g SH2.g SB-1
YOHO,SMEOL,ox | Yield of OHOs on methanol under aerobic conditions | 0.4 | g XOHO.g SMEOL-1
YMEOLO | Yield of MEOLOs on methanol | 0.4 | g XMEOLO.g SMEOL-1
YPAO,PHA,ox | Yield of PAOs on PHA under aerobic conditions | 0.639 | g XPAO.g XPHA-1
YPAO,PHA,anox | Yield of PAOs on PHA under anoxic conditions | 0.52 | g XPAO.g XPHA-1
YPAO,SB,ana | Yield of PAOs on readily biodegradable substrate under anaerobic conditions | 0.1 | g XPAO.g SB-1
YPAO,H2,ana,high | Yield of H2 production in fermentation with high VFA concentration (PAO) | 0.35 | g SH2.g SB-1
YPAO,H2,ana,low | Yield of H2 production in fermentation with low VFA concentration (PAO) | 0.1 | g SH2.g SB-1
fPP,PHA,ox | Ratio of PP stored per PHA consumed under aerobic conditions | 0.92 | g XPP.g XPHA-1
fPP,PHA,anox | Ratio of PP stored per PHA consumed under anoxic conditions | 0.55 | g XPP.g XPHA-1
fP,VFA | Ratio of P released per VFA stored | 0.65 | g XPP.g SVFA-1
iTSS,PP | TSS content of PP | 3.5161 | g XTSS.g XPP-1
YGAO,GLY,ox | Yield of GAOs on glycogen under aerobic conditions | 0.6 | g XGAO.g XGLY-1
YGAO,GLY,anox | Yield of GAOs on glycogen under anoxic conditions | 0.5 | g XGAO.g XGLY-1
YNITO | Yield of NITOs on NHx | 0.24 | g XNITO.g SNHx-1
YAMETO | Yield of AMETOs on VFA | 0.1 | g XAMETO.g SVFA-1
YHMETO | Yield of HMETOs on H2 | 0.1 | g XHMETO.g SH2-1
General stoichiometry
Symbol | Name | Value | Unit | Comment
fE | Fraction of endogenous products produced in biomass decay | 0.08 | g XE.g XBIO-1
iN,BIO | N content of biomasses | 0.07 | g N.g COD-1
iN,XE | N content of endogenous products | 0.06 | g N.g COD-1
iN,CB | N content of colloidal biodegradable substrate | 0.03 | g N.g COD-1
iN,CU | N content of colloidal unbiodegradable organics | 0.01 | g N.g COD-1
iN,SU | N content of soluble unbiodegradable organics | 0.05 | g N.g COD-1
iN,XSTR | N content of struvite | 0.057076 | g N.g TSS-1 | A_MN/M_MSTR
iP,BIO | P content of biomasses | 0.02 | g P.g COD-1
iP,CB | P content of colloidal biodegradable substrate | 0.005 | g P.g COD-1
iP,CU | P content of colloidal unbiodegradable organics | 0.005 | g P.g COD-1
iP,SU | P content of soluble unbiodegradable organics | 0.002 | g P.g COD-1
iP,XSTR | P content of struvite | 0.12621 | g P.g TSS-1 | A_MP/M_MSTR
iP,XACP | P content of ACP | 0.16207 | g P.g TSS-1 | 2*A_MP/M_MACP
iP,XVivi | P content of vivianite | 0.1235 | g P.g TSS-1 | 2*A_MP/M_MVivi
iCV,XB | COD of biodegradable substrate in volatile solids | 1.8 | g COD.g VSS-1
iCV,XU | COD of particulate unbiodegradable organics in volatile solids | 1.3 | g COD.g VSS-1
iCV,BIO | COD of biomass in volatile solids | 1.42 | g COD.g VSS-1
iCV,XE | COD of endogenous products in volatile solids | 1.42 | g COD.g VSS-1
iCV,VFA | COD of VFA in volatile solids | 1.066 | g COD.g VS-1
iCV,SB | COD of readily biodegradable substrate in volatile solids | 1.066 | g COD.g VS-1
iCV,MEOL | COD of methanol in volatile solids | 1.5 | g COD.g VS-1
iCV,SU | COD of soluble unbiodegradable organics in volatile solids | 0.926 | g COD.g VS-1
iCV,CB | COD of colloidal biodegradable substrate in volatile solids | 1.8 | g COD.g VS-1
iCV,CU | COD of colloidal unbiodegradable organics in volatile solids | 1.3 | g COD.g VS-1
iCV,PHA | COD of PHA in volatile solids | 1.67 | g COD.g VSS-1
iCV,GLY | COD of glycogen in volatile solids | 1.19 | g COD.g VSS-1
iCIT,BIO | Inorganic carbon content of biomass | 0.352 | g TIC.g COD-1 | C5H7O2N: 32 g COD/mol C
iCIT,SB | Inorganic carbon content of SB and SU | 0.286 | g TIC.g COD-1 | C5H7O2N: 32 g COD/mol C
iCIT,MEOL | Inorganic carbon content of methanol | 0.25 | g TIC.g COD-1 | CH4O: 48 g COD/mol C
iCIT,CH4 | Inorganic carbon content of CH4 | 0.188 | g TIC.g COD-1 | CH4: 64 g COD/mol C
iCIT,VFA | Inorganic carbon content of VFA | 0.375 | g TIC.g COD-1 | C2H4O2: 32 g COD/mol C
iCIT,PHA | Inorganic carbon content of PHA | 0.333 | g TIC.g COD-1 | H[C4H6O2]nOH: 36 g COD/mol C
iCIT,GLY | Inorganic carbon content of glycogen | 0.375 | g TIC.g COD-1 | [C6H10O5]n: 32 g COD/mol C
iINORG | Inorganic content of biomass | 0.11 | g TSS.g COD-1 | 15% of VSS - Ekama
iCa,PP | Calcium content of PP | 0.1 | mol Ca.mol P-1 | Comeau et al. (1986) Wat Res vol 20 N°12
iMg,PP | Magnesium content of PP | 0.35 | mol Mg.mol P-1 | Comeau et al. (1986) Wat Res vol 20 N°12
iK,PP | Potassium content of PP | 0.1 | mol K.mol P-1 | Comeau et al. (1986) Wat Res vol 20 N°12
iCAT,P | Cation content of SP,B | 0 | g Na.g P-1
fNa | Fraction of Na in NaCl | 0.39337 | g Na.g NaCl-1
BOD stoichiometry
Symbol | Name | Value | Unit | Comment
YBOD,ult | Yield on ultimate BOD | 0.95 | g O2.g COD-1
fS,BOD5,BODult | Fraction of BOD5 to ultimate BOD in soluble biodegradable substrates | 0.9
fC,BOD5,BODult | Fraction of BOD5 to ultimate BOD in colloidal biodegradable substrates | 0.6
fX,BOD5,BODult | Fraction of BOD5 to ultimate BOD in particulate biodegradable substrates | 0.5
HFO stoichiometry
Symbol | Name | Value | Unit | Comment
ASFH | Active site factor for HFO,H | 1.2 | mol P.mol Fe-1
ASFL | Active site factor for HFO,L | 0.2 | mol P.mol Fe-1
fH2O,HFO,TSS | Fraction of H2O loss in TSS test for HFO | 0.0829 | g H2O.g FeOH-1
fH2O,HFO,VSS | Fraction of H2O loss in VSS test for HFO | 0.17 | g H2O.g FeOH-1 | Me(OH)3 -> Me2O3 + 3H2O
Aluminium phosphate precipitation stoichiometry
Symbol | Name | Value | Unit | Comment
fP,Al | Fraction of P per Al in AlP | 1.148 | g P.g AlP-1
fH2O,AlOH,TSS | Fraction of H2O loss in TSS test for AlOH | 0.1135 | g H2O.g AlOH-1
fH2O,AlOH,VSS | Fraction of H2O loss in VSS test for AlOH | 0.2329 | g H2O.g AlOH-1
Parameters for gas transfer
Symbol | Name | Value | Unit | Comment
kL,GO2,bub | Liquid-side mass transfer coefficient of O2 for gas bubbles | 13 | m/d
kL,GO2,sur | Liquid-side mass transfer coefficient of O2 at liquid surface | 7.6 | m/d
fkL,GN2 | Correction factor for mass transfer of N2 | 100 | %
fkL,GCO2 | Correction factor for mass transfer of CO2 | 100 | %
fkL,GCH4 | Correction factor for mass transfer of CH4 | 100 | %
fkL,GH2 | Correction factor for mass transfer of H2 | 100 | %
fkL,GNH3 | Correction factor for mass transfer of NH3 | 5 | % | Used to compensate for the high solubility of NH3 gas
Oxidation-reduction potential constants
Symbol | Name | Value | Unit | Comment
ORPbase | Base ORP value | -300 | mV
ORPmax,SO2 | ORP max for dissolved oxygen | 300 | mV
ORPmax,SNOx | ORP max for dissolved nitrate | 70 | mV
KORP,SO2 | Half-saturation of dissolved oxygen for ORP | 0.05 | g O2/m3
KORP,SNOx | Half-saturation of NOx for ORP | 0.1 | g N/m3
KORP,CH4 | Half-saturation of dissolved methane for ORP | 1.5 | g COD/m3
IS correction factor
Symbol | Name | Value | Unit | Comment
ISlim | IS cut-off threshold for Davies activity coefficient correction | 0.2 | ISunit | The fmono/fdi/ftri curves have minima at 0.3 and literally couldn't be used above that
SlopeIS,corr | Slope of correction | -0.001

## Influent
Unit overview
Name: | Influent
Sumo name: | Influent
Category: | Flow - energy elements
Unit: | Influent
Type: | Sumo1 concentration based influent
Settings
Influent specifications
Symbol | Name | Value | Unit | Comment
Q | Flow rate | 18446 | m3/d
TCOD | Total COD | 381 | g COD/m3
TKN | Total Kjeldahl nitrogen | 54 | g N/m3
TP | Total phosphorus | 8 | g P/m3
T | Temperature | 20 | °C
Influent fractions
Symbol | Name | Value | Unit | Comment
frSCCOD,TCOD | Fraction of filtered COD (SCCOD, 1.5 µm, incl. colloids) in total COD | 44.6 | %
frSCOD,TCOD | Fraction of flocculated filtered (SCOD, wo colloids) COD in total COD | 22.3 | %
frVSS,TSS | Fraction of VSS/TSS | 84.8649 | %
frVFA,SCCOD | Fraction of VFA in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.7647 | %
frSU,SCCOD | Fraction of soluble unbiodegradable organics (SU) in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.7647 | % | Fraction of filtered COD, not total COD!
frXU,TCOD | Fraction of particulate unbiodegradable organics (XU) in total COD | 14 | %
frXOHO,TCOD | Fraction of heterotrophs (OHO) in total COD | 5 | %
frXE,XOHO | Fraction of endogenous products (XE) of OHOs | 20 | %
frCU,CCOD | Fraction of colloidal unbiodegradable organics (CU) in colloidal COD | 20 | %
frSNHx,TKN | Fraction of NHx in total Kjeldahl nitrogen (TKN) | 69.7674 | %
frSPO4,TP | Fraction of PO4 in total phosphorus (TP) | 58.1395 | %
frN,SB | Fraction of N in readily biodegradable substrate (SB) | 4 | %
frN,XU | Fraction of N in particulate unbiodegradable substrate (XU) | 1 | %
frP,SB | Fraction of P in readily biodegradable substrate (SB) | 1 | %
frP,XU | Fraction of P in particulate unbiodegradable substrate (XU) | 0.1 | %
Ionic components
Symbol | Name | Value | Unit | Comment
SCa | Calcium | 150 | g Ca/m3
SMg | Magnesium | 15 | g Mg/m3
SK | Potassium | 16 | g K/m3
SAN | Other strong anions (as Cl-) | 300 | g Cl/m3
SCAT | Other strong cations (as Na+) | 109.9 | g Na/m3
Other influent constituents (usually zero)
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) | 1e-40 | g O2/m3
SMEOL | Methanol (MEOL) | 1e-40 | g COD/m3
XPHA | Stored polyhydroxyalkanoates (PHA) | 1e-40 | g COD/m3
XGLY | Stored glycogen (GLY) | 1e-40 | g COD/m3
XE,ana | Anaerobic endogenous decay products | 1e-40 | g COD/m3
XPAO | Phosphorus accumulating organisms (PAO) | 0.1 | g COD/m3
XGAO | Glycogen accumulating organisms (GAO) | 0.1 | g COD/m3
XMEOLO | Anoxic methanol utilizers (MEOLO) | 0.1 | g COD/m3
XNITO | Aerobic nitrifying organisms (NITO) | 0.1 | g COD/m3
XAMETO | Acidoclastic methanogens (AMETO) | 0.1 | g COD/m3
XHMETO | Hydrogenotrophic methanogens (HMETO) | 0.1 | g COD/m3
SNOx | Nitrate and nitrite (NOx) | 1e-40 | g N/m3
SN2 | Dissolved nitrogen (N2) | 16 | g N/m3
XPP | Stored polyphosphate (PP) | 1e-40 | g P/m3
SCH4 | Dissolved methane (CH4) | 1e-40 | g COD/m3
SH2 | Dissolved hydrogen (H2) | 1e-40 | g COD/m3
SFe3 | Ferric ion (Fe3) | 1e-40 | g Fe/m3
SFe2 | Ferrous ion (Fe2) | 1e-40 | g Fe/m3
XHFO,old | Aged unused hydrous ferric oxide (HFO,old) | 1e-40 | g Fe/m3
XHFO,H,P | P-bound hydrous ferric oxide, high surface (HFO,H,P) | 1e-40 | g Fe/m3
XHFO,L,P | P-bound hydrous ferric oxide, low surface (HFO,L,P) | 1e-40 | g Fe/m3
XHFO,H,P,old | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) | 1e-40 | g Fe/m3
XHFO,L,P,old | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) | 1e-40 | g Fe/m3
XAlOH | Aluminium hydroxide compounds (AlOH) | 1e-40 | g Al/m3
XAlP | Aluminium phosphate compounds (AlP) | 1e-40 | g Al/m3
XCaCO3 | Calcium carbonate (CaCO3) | 1e-40 | g TSS/m3
XACP | Amorphous calcium phosphate (ACP) | 1e-40 | g TSS/m3
XSTR | Struvite (STR) | 1e-40 | g TSS/m3
XVivi | Vivianite (Vivi) | 1e-40 | g TSS/m3
Total inorganic carbon (CO2)
Symbol | Name | Value | Unit | Comment
SCO2 | Total inorganic carbon (CO2) | 90 | g TIC/m3
Mixing - precipitation parameters
Symbol | Name | Value | Unit | Comment
G | Average velocity gradient in mixing tank | 425 | 1/s
KG | Half-saturation for G value | 45 | 1/s
Dry influent | Enabled
No interpolation
Time | Q | TCOD | TKN
d | m3.d-1 | g COD.m-3 | g N.m-3
0 | 18446 | 381.19 | 54.4256
0.010417 | 18446 | 381.19 | 54.4256
0.020833 | 18446 | 381.19 | 54.4256
0.03125 | 18446 | 381.19 | 54.4256
0.041667 | 18446 | 381.19 | 54.4256
0.052083 | 18446 | 381.19 | 54.4256
0.0625 | 18446 | 381.19 | 54.4256
0.072917 | 18446 | 381.19 | 54.4256
0.083333 | 18446 | 381.19 | 54.4256
0.09375 | 18446 | 381.19 | 54.4256
0.10417 | 18446 | 381.19 | 54.4256
0.11458 | 18446 | 381.19 | 54.4256
0.125 | 18446 | 381.19 | 54.4256
0.13542 | 18446 | 381.19 | 54.4256
0.14583 | 18446 | 381.19 | 54.4256
0.15625 | 18446 | 381.19 | 54.4256
0.16667 | 18446 | 381.19 | 54.4256
0.17708 | 18446 | 381.19 | 54.4256
0.1875 | 18446 | 381.19 | 54.4256
0.19792 | 18446 | 381.19 | 54.4256
0.20833 | 18446 | 381.19 | 54.4256
0.21875 | 18446 | 381.19 | 54.4256
0.22917 | 18446 | 381.19 | 54.4256
0.23958 | 18446 | 381.19 | 54.4256
0.25 | 18446 | 381.19 | 54.4256
0.26042 | 18446 | 381.19 | 54.4256
0.27083 | 18446 | 381.19 | 54.4256
0.28125 | 18446 | 381.19 | 54.4256
0.29167 | 18446 | 381.19 | 54.4256
0.30208 | 18446 | 381.19 | 54.4256
0.3125 | 18446 | 381.19 | 54.4256
0.32292 | 18446 | 381.19 | 54.4256
0.33333 | 18446 | 381.19 | 54.4256
0.34375 | 18446 | 381.19 | 54.4256
0.35417 | 18446 | 381.19 | 54.4256
0.36458 | 18446 | 381.19 | 54.4256
0.375 | 18446 | 381.19 | 54.4256
0.38542 | 18446 | 381.19 | 54.4256
0.39583 | 18446 | 381.19 | 54.4256
0.40625 | 18446 | 381.19 | 54.4256
0.41667 | 18446 | 381.19 | 54.4256
0.42708 | 18446 | 381.19 | 54.4256
0.4375 | 18446 | 381.19 | 54.4256
0.44792 | 18446 | 381.19 | 54.4256
0.45833 | 18446 | 381.19 | 54.4256
0.46875 | 18446 | 381.19 | 54.4256
0.47917 | 18446 | 381.19 | 54.4256
0.48958 | 18446 | 381.19 | 54.4256
0.5 | 18446 | 381.19 | 54.4256
0.51042 | 18446 | 381.19 | 54.4256
0.52083 | 18446 | 381.19 | 54.4256
0.53125 | 18446 | 381.19 | 54.4256
0.54167 | 18446 | 381.19 | 54.4256
0.55208 | 18446 | 381.19 | 54.4256
0.5625 | 18446 | 381.19 | 54.4256
0.57292 | 18446 | 381.19 | 54.4256
0.58333 | 18446 | 381.19 | 54.4256
0.59375 | 18446 | 381.19 | 54.4256
0.60417 | 18446 | 381.19 | 54.4256
0.61458 | 18446 | 381.19 | 54.4256
0.625 | 18446 | 381.19 | 54.4256
0.63542 | 18446 | 381.19 | 54.4256
0.64583 | 18446 | 381.19 | 54.4256
0.65625 | 18446 | 381.19 | 54.4256
0.66667 | 18446 | 381.19 | 54.4256
0.67708 | 18446 | 381.19 | 54.4256
0.6875 | 18446 | 381.19 | 54.4256
0.69792 | 18446 | 381.19 | 54.4256
0.70833 | 18446 | 381.19 | 54.4256
0.71875 | 18446 | 381.19 | 54.4256
0.72917 | 18446 | 381.19 | 54.4256
0.73958 | 18446 | 381.19 | 54.4256
0.75 | 18446 | 381.19 | 54.4256
0.76042 | 18446 | 381.19 | 54.4256
0.77083 | 18446 | 381.19 | 54.4256
0.78125 | 18446 | 381.19 | 54.4256
0.79167 | 18446 | 381.19 | 54.4256
0.80208 | 18446 | 381.19 | 54.4256
0.8125 | 18446 | 381.19 | 54.4256
0.82292 | 18446 | 381.19 | 54.4256
0.83333 | 18446 | 381.19 | 54.4256
0.84375 | 18446 | 381.19 | 54.4256
0.85417 | 18446 | 381.19 | 54.4256
0.86458 | 18446 | 381.19 | 54.4256
0.875 | 18446 | 381.19 | 54.4256
0.88542 | 18446 | 381.19 | 54.4256
0.89583 | 18446 | 381.19 | 54.4256
0.90625 | 18446 | 381.19 | 54.4256
0.91667 | 18446 | 381.19 | 54.4256
0.92708 | 18446 | 381.19 | 54.4256
0.9375 | 18446 | 381.19 | 54.4256
0.94792 | 18446 | 381.19 | 54.4256
0.95833 | 18446 | 381.19 | 54.4256
0.96875 | 18446 | 381.19 | 54.4256
0.97917 | 18446 | 381.19 | 54.4256
0.98958 | 18446 | 381.19 | 54.4256
1 | 18446 | 381.19 | 54.4256
1.0104 | 21474 | 405.8761 | 54.2133
1.0208 | 19620 | 399.9887 | 54.459
1.0312 | 19334 | 394.8652 | 54.7792
1.0417 | 18978 | 391.7643 | 56.1501
1.0521 | 18321 | 388.4407 | 57.984
1.0625 | 17855 | 398.9015 | 61.4396
1.0729 | 17237 | 388.4907 | 60.8017
1.0833 | 16453 | 375.3283 | 58.8446
1.0937 | 16548 | 365.2611 | 57.828
1.1042 | 16295 | 353.3523 | 54.8502
1.1146 | 14743 | 341.9295 | 54.3289
1.125 | 14743 | 341.9295 | 54.3289
1.1354 | 13613 | 320.789 | 50.0572
1.1458 | 12807 | 308.9749 | 47.2126
1.1562 | 12173 | 292.4167 | 43.2385
1.1667 | 11533 | 276.7106 | 39.8134
1.1771 | 12198 | 266.7912 | 37.9419
1.1875 | 11640 | 256.3903 | 36.0749
1.1979 | 11978 | 247.4693 | 33.6307
1.2083 | 13272 | 246.0487 | 33.9029
1.2187 | 12452 | 242.0061 | 33.817
1.2292 | 13453 | 240.7754 | 33.8495
1.2396 | 13815 | 241.0834 | 33.8232
1.25 | 13803 | 240.4174 | 33.7176
1.2604 | 12542 | 233.4357 | 33.0814
1.2708 | 11865 | 228.794 | 32.7439
1.2812 | 12118 | 225.7178 | 32.3479
1.2917 | 11906 | 222.5619 | 32.032
1.3021 | 12059 | 220.6651 | 31.9285
1.3125 | 12446 | 220.0539 | 32.0348
1.3229 | 12982 | 220.9957 | 32.4383
1.3333 | 12956 | 221.5555 | 32.8965
1.3437 | 12745 | 221.8627 | 33.279
1.3542 | 13597 | 224.4969 | 33.9482
1.3646 | 14171 | 229.2495 | 34.8338
1.375 | 14171 | 229.2495 | 34.8338
1.3854 | 17637 | 242.4853 | 38.5688
1.3958 | 17635 | 264.3305 | 45.2445
1.4062 | 22461 | 298.6008 | 52.6706
1.4167 | 26276 | 337.0767 | 59.3141
1.4271 | 25598 | 375.3989 | 67.5693
1.4375 | 27780 | 413.6961 | 73.7548
1.4479 | 29551 | 452.3604 | 79.3185
1.4583 | 31861 | 486.992 | 82.7013
1.4687 | 32171 | 512.0381 | 83.4993
1.4792 | 32180 | 527.0729 | 80.6565
1.4896 | 31869 | 534.6193 | 75.81
1.5 | 28047 | 530.6415 | 72.7503
1.5104 | 26690 | 514.1164 | 66.1859
1.5208 | 25572 | 503.5321 | 63.0469
1.5312 | 25496 | 496.7603 | 61.0328
1.5417 | 22401 | 482.346 | 58.5822
1.5521 | 26555 | 487.1721 | 58.9774
1.5625 | 25905 | 488.1841 | 58.195
1.5729 | 24310 | 483.7227 | 57.1044
1.5833 | 23404 | 478.1805 | 56.8374
1.5937 | 20560 | 463.8056 | 54.995
1.6042 | 18732 | 443.9218 | 53.4856
1.6146 | 25320 | 451.2177 | 53.7971
1.625 | 25320 | 451.2177 | 53.7971
1.6354 | 23046 | 445.7112 | 52.6887
1.6458 | 21357 | 436.3312 | 51.9174
1.6562 | 22487 | 433.8326 | 52.4168
1.6667 | 18221 | 417.8163 | 51.3897
1.6771 | 17442 | 402.0527 | 50.2781
1.6875 | 19246 | 397.5336 | 50.6766
1.6979 | 19197 | 394.7309 | 51.5771
1.7083 | 19637 | 392.3673 | 51.4381
1.7187 | 19014 | 386.3575 | 50.3783
1.7292 | 18480 | 376.4667 | 48.5387
1.7396 | 18208 | 368.1866 | 47.8773
1.75 | 18547 | 364.4546 | 47.7202
1.7604 | 18670 | 363.4811 | 49.5326
1.7708 | 18654 | 364.512 | 50.6437
1.7812 | 23137 | 376.5412 | 53.2088
1.7917 | 22509 | 383.8079 | 53.4958
1.8021 | 22031 | 388.1579 | 51.2442
1.8125 | 22489 | 398.1006 | 53.6977
1.8229 | 18876 | 391.6764 | 52.9122
1.8333 | 20674 | 394.1391 | 53.8248
1.8437 | 24145 | 409.7801 | 57.1672
1.8542 | 22518 | 417.2129 | 59.166
1.8646 | 22803 | 423.2762 | 60.1623
1.875 | 22803 | 423.2762 | 60.1623
1.8854 | 21780 | 426.0904 | 61.6272
1.8958 | 19067 | 420.0501 | 61.441
1.9062 | 26211 | 439.1423 | 63.4727
1.9167 | 24096 | 445.1928 | 63.0497
1.9271 | 23071 | 445.77 | 63.1375
1.9375 | 22388 | 443.6998 | 62.7881
1.9479 | 17483 | 424.9806 | 60.6968
1.9583 | 25814 | 438.8149 | 62.1559
1.9687 | 23248 | 438.9955 | 60.8938
1.9792 | 24098 | 440.2235 | 59.4942
1.9896 | 22402 | 435.9397 | 57.6494
2 | 19962 | 424.6631 | 55.7783
2.0104 | 18618 | 398.5001 | 53.4007
2.0208 | 19046 | 393.3037 | 54.0075
2.0312 | 23433 | 403.8392 | 55.8545
2.0417 | 22011 | 408.2183 | 57.4939
2.0521 | 23310 | 417.4127 | 60.3045
2.0625 | 23158 | 425.6805 | 63.6883
2.0729 | 15122 | 402.2217 | 61.2693
2.0833 | 15319 | 383.3403 | 59.1363
2.0937 | 15342 | 368.6021 | 57.8635
2.1042 | 14751 | 351.8203 | 54.5865
2.1146 | 14287 | 339.7802 | 54.1525
2.125 | 14287 | 339.7802 | 54.1525
2.1354 | 12478 | 319.354 | 49.8604
2.1458 | 12477 | 306.9709 | 47.074
2.1562 | 11347 | 288.3867 | 42.9496
2.1667 | 11037 | 272.1576 | 39.5317
2.1771 | 10473 | 258.0312 | 37.3391
2.1875 | 10000 | 244.7083 | 35.3368
2.1979 | 11258 | 236.1183 | 32.9808
2.2083 | 10436 | 228.5797 | 32.7737
2.2187 | 10976 | 223.7151 | 32.7521
2.2292 | 11250 | 219.4524 | 32.5682
2.2396 | 11740 | 217.5834 | 32.4339
2.25 | 11562 | 214.5434 | 32.1927
2.2604 | 12578 | 214.1457 | 32.0666
2.2708 | 11399 | 210.8371 | 31.773
2.2812 | 11448 | 208.3329 | 31.3923
2.2917 | 12090 | 208.1039 | 31.2846
2.3021 | 12429 | 209.0751 | 31.3436
2.3125 | 11500 | 207.2499 | 31.3023
2.3229 | 11717 | 206.5487 | 31.5964
2.3333 | 11751 | 206.0575 | 32.0027
2.3437 | 11489 | 205.3916 | 32.3337
2.3542 | 12859 | 208.553 | 33.0549
2.3646 | 12350 | 210.6715 | 33.7288
2.375 | 12350 | 210.6715 | 33.7288
2.3854 | 12194 | 215.6123 | 36.7541
2.3958 | 15329 | 235.4465 | 43.5038
2.4062 | 22901 | 274.7928 | 51.343
2.4167 | 23690 | 308.4187 | 57.3951
2.4271 | 24749 | 348.2379 | 65.8921
2.4375 | 27249 | 388.5991 | 72.1992
2.4479 | 29504 | 430.6684 | 78.0019
2.4583 | 31868 | 471.119 | 81.728
2.4687 | 32126 | 501.0931 | 82.8186
2.4792 | 31909 | 519.7029 | 80.1566
2.4896 | 31927 | 531.4913 | 75.6279
2.5 | 31719 | 540.9305 | 74.0525
2.5104 | 27039 | 534.3184 | 67.4458
2.5208 | 25844 | 522.5491 | 64.2126
2.5312 | 25174 | 510.6373 | 61.7853
2.5417 | 24783 | 502.4139 | 60.1624
2.5521 | 24444 | 495.2881 | 59.0782
2.5625 | 22762 | 484.3461 | 57.4217
2.5729 | 24940 | 484.5897 | 57.265
2.5833 | 24113 | 481.7965 | 57.1684
2.5937 | 23320 | 476.5376 | 56.182
2.6042 | 22247 | 467.7558 | 55.3934
2.6146 | 21875 | 456.8897 | 53.5688
2.625 | 21875 | 456.8897 | 53.5688
2.6354 | 21863 | 447.2112 | 52.5853
2.6458 | 21236 | 438.0462 | 51.995
2.6562 | 21473 | 432.2246 | 52.1678
2.6667 | 20822 | 426.1333 | 52.244
2.6771 | 20463 | 420.4427 | 51.7382
2.6875 | 20034 | 415.8836 | 51.8146
2.6979 | 19328 | 411.4279 | 52.5267
2.7083 | 18928 | 403.5123 | 51.9631
2.7187 | 18510 | 394.2915 | 50.7516
2.7292 | 18319 | 383.0207 | 48.8803
2.7396 | 18224 | 375.8796 | 48.3045
2.75 | 19106 | 372.8276 | 48.2564
2.7604 | 21604 | 388.2901 | 51.3019
2.7708 | 22228 | 395.84 | 52.869
2.7812 | 21169 | 395.2933 | 54.0189
2.7917 | 19849 | 391.4279 | 53.5743
2.8021 | 17451 | 380.7979 | 50.2302
2.8125 | 18335 | 380.4816 | 52.158
2.8229 | 22018 | 389.4494 | 53.2013
2.8333 | 23369 | 400.7131 | 54.563
2.8437 | 23270 | 411.3441 | 57.1361
2.8542 | 25050 | 426.9039 | 60.0863
2.8646 | 21540 | 426.3132 | 60.1561
2.875 | 21540 | 426.3132 | 60.1561
2.8854 | 19321 | 420.6094 | 60.9717
2.8958 | 21190 | 423.6741 | 61.9397
2.9062 | 26591 | 443.1753 | 63.7658
2.9167 | 24225 | 448.8688 | 63.2819
2.9271 | 23902 | 451.657 | 63.6021
2.9375 | 24339 | 455.0398 | 63.7372
2.9479 | 21529 | 447.4716 | 62.5475
2.9583 | 26978 | 460.1359 | 63.5916
2.9687 | 25693 | 464.3935 | 62.7504
2.9792 | 24779 | 462.8136 | 60.9135
2.9896 | 24086 | 460.1727 | 59.3084
3 | 23308 | 455.7101 | 58.0596
3.0104 | 21014 | 433.3151 | 55.7004
3.0208 | 19118 | 405.8737 | 54.7168
3.0312 | 18847 | 406.2652 | 55.3458
3.0417 | 18509 | 402.7483 | 56.6962
3.0521 | 17886 | 400.4607 | 58.5891
3.0625 | 17445 | 399.2405 | 61.4037
3.0729 | 16858 | 392.9787 | 60.9977
3.0833 | 16116 | 396.4353 | 59.9493
3.0937 | 16206 | 383.4361 | 58.775
3.1042 | 15965 | 368.3253 | 55.6244
3.1146 | 14494 | 359.9292 | 55.2555
3.125 | 14494 | 359.9292 | 55.2555
3.1354 | 13423 | 344.187 | 51.2796
3.1458 | 12660 | 333.8499 | 48.5108
3.1562 | 12059 | 317.0577 | 44.5214
3.1667 | 11453 | 300.8306 | 41.0666
3.1771 | 12083 | 286.6642 | 38.9758
3.1875 | 11554 | 272.8983 | 36.9315
3.1979 | 11875 | 262.4013 | 34.405
3.2083 | 13101 | 254.1727 | 34.3194
3.2187 | 12323 | 248.2211 | 34.1346
3.2292 | 13271 | 246.1034 | 34.118
3.2396 | 13614 | 242.0434 | 33.8589
3.25 | 13604 | 240.7554 | 33.7206
3.2604 | 12408 | 240.4567 | 33.4415
3.2708 | 11767 | 236.2431 | 33.1271
3.2812 | 12006 | 233.0128 | 32.7229
3.2917 | 11805 | 228.5169 | 32.3364
3.3021 | 11951 | 225.9311 | 32.1976
3.3125 | 12317 | 223.0869 | 32.1857
3.3229 | 12825 | 221.2077 | 32.4389
3.3333 | 12800 | 220.6275 | 32.8368
3.3437 | 12600 | 221.9566 | 33.2747
3.3542 | 13408 | 222.8049 | 33.845
3.3646 | 13952 | 223.9355 | 34.5356
3.375 | 13952 | 223.9355 | 34.5356
3.3854 | 17235 | 230.8373 | 37.9001
3.3958 | 17233 | 245.1775 | 44.1624
3.4062 | 21804 | 265.1568 | 50.7095
3.4167 | 25418 | 284.4257 | 56.145
3.4271 | 24776 | 322.0049 | 64.367
3.4375 | 26842 | 362.7951 | 70.6261
3.4479 | 28519 | 395.6424 | 75.7771
3.4583 | 30707 | 427.852 | 78.9243
3.4687 | 31000 | 456.0231 | 79.8884
3.4792 | 31009 | 478.9799 | 77.5175
3.4896 | 30713 | 495.3973 | 73.2112
3.5 | 27093 | 509.6345 | 71.3304
3.5104 | 25808 | 516.9674 | 66.1931
3.5208 | 24748 | 510.4691 | 63.3037
3.5312 | 24677 | 503.0543 | 61.2522
3.5417 | 21745 | 495.8899 | 59.239
3.5521 | 25678 | 493.2741 | 59.1811
3.5625 | 25062 | 480.6961 | 57.6101
3.5729 | 23552 | 487.0767 | 57.1669
3.5833 | 22693 | 489.3655 | 57.3575
3.5937 | 20001 | 485.2256 | 56.1043
3.6042 | 18269 | 478.2708 | 55.3134
3.6146 | 24508 | 460.1237 | 54.1847
3.625 | 24508 | 460.1237 | 54.1847
3.6354 | 22354 | 437.1342 | 52.0876
3.6458 | 20755 | 445.6882 | 52.3517
3.6562 | 21824 | 442.8895 | 52.8289
3.6667 | 17785 | 435.8393 | 52.3177
3.6771 | 17047 | 434.9827 | 52.0261
3.6875 | 18755 | 420.7456 | 51.8986
3.6979 | 18708 | 407.6079 | 52.2271
3.7083 | 19125 | 400.6303 | 51.8303
3.7187 | 18535 | 392.7755 | 50.6708
3.7292 | 18029 | 386.2027 | 49.018
3.7396 | 17772 | 380.6086 | 48.5057
3.75 | 18093 | 374.1766 | 48.2
3.7604 | 18209 | 367.5061 | 49.6982
3.7708 | 18193 | 368.129 | 50.7874
3.7812 | 22437 | 365.3062 | 52.4771
3.7917 | 21842 | 363.4009 | 52.2469
3.8021 | 21390 | 376.1009 | 50.4752
3.8125 | 21824 | 387.9146 | 53.0275
3.8229 | 18403 | 393.2404 | 52.9362
3.8333 | 20104 | 400.0661 | 54.082
3.8437 | 23390 | 396.2871 | 56.2854
3.8542 | 21850 | 401.2219 | 58.1622
3.8646 | 22120 | 415.2362 | 59.6067
3.875 | 22120 | 415.2362 | 59.6067
3.8854 | 21151 | 421.5534 | 61.2805
3.8958 | 18582 | 428.3361 | 61.8339
3.9062 | 25345 | 429.7403 | 62.7953
3.9167 | 23343 | 421.5688 | 61.576
3.9271 | 22372 | 438.576 | 62.6222
3.9375 | 21725 | 442.8588 | 62.641
3.9479 | 17083 | 442.4236 | 61.5958
3.9583 | 24968 | 439.3459 | 62.0609
3.9687 | 22540 | 420.3625 | 59.7205
3.9792 | 23343 | 432.8236 | 58.9533
3.9896 | 21738 | 432.7157 | 57.3657
4 | 19429 | 435.7362 | 56.3188
4.0104 | 18156 | 418.7301 | 54.4544
4.0208 | 18561 | 406.6767 | 54.6824
4.0312 | 22713 | 398.8902 | 55.4699
4.0417 | 21366 | 396.0663 | 56.7138
4.0521 | 22596 | 409.4287 | 59.7438
4.0625 | 22452 | 415.6835 | 63.0135
4.0729 | 14847 | 421.9307 | 62.2922
4.0833 | 15033 | 423.1963 | 61.2461
4.0937 | 15055 | 397.1581 | 59.3662
4.1042 | 14496 | 376.3303 | 55.8715
4.1146 | 14056 | 363.2672 | 55.3816
4.125 | 14056 | 363.2672 | 55.3816
4.1354 | 12345 | 342.654 | 51.0731
4.1458 | 12344 | 331.9259 | 48.3744
4.1562 | 11274 | 315.6217 | 44.3627
4.1667 | 10981 | 298.8276 | 40.915
4.1771 | 10448 | 282.6362 | 38.6115
4.1875 | 10000 | 268.3473 | 36.5567
4.1979 | 11190 | 253.6453 | 33.8895
4.2083 | 10412 | 242.4967 | 33.4925
4.2187 | 10923 | 236.8771 | 33.4322
4.2292 | 11182 | 228.6434 | 33.0422
4.2396 | 11646 | 223.7624 | 32.7508
4.25 | 11478 | 219.4434 | 32.4442
4.2604 | 12439 | 214.5957 | 32.0814
4.2708 | 11323 | 213.56 | 31.91
4.2812 | 11370 | 213.7329 | 31.6694
4.2917 | 11977 | 210.5689 | 31.4074
4.3021 | 12298 | 208.5541 | 31.3076
4.3125 | 11419 | 208.6369 | 31.3696
4.3229 | 11624 | 209.6226 | 31.751
4.3333 | 11656 | 207.8295 | 32.0901
4.3437 | 11409 | 207.5177 | 32.4399
4.3542 | 12704 | 207.3159 | 32.9796
4.3646 | 12223 | 207.4735 | 33.553
4.375 | 12223 | 207.4735 | 33.553
4.3854 | 12076 | 214.9023 | 36.7102
4.3958 | 15040 | 226.6095 | 43.0091
4.4062 | 22202 | 238.2968 | 49.2052
4.4167 | 22948 | 255.5587 | 54.2938
4.4271 | 23950 | 298.2109 | 62.9163
4.4375 | 26314 | 334.1531 | 68.8839
4.4479 | 28447 | 368.4974 | 74.1426
4.4583 | 30682 | 402.767 | 77.3936
4.4687 | 30926 | 434.3411 | 78.5554
4.4792 | 30720 | 463.1119 | 76.5077
4.4896 | 30737 | 484.4543 | 72.5487
4.5 | 30540 | 502.2645 | 71.479
4.5104 | 26113 | 527.2454 | 66.8543
4.5208 | 24983 | 533.0601 | 64.6641
4.5312 | 24349 | 523.2403 | 62.3649
4.5417 | 23979 | 514.893 | 60.7385
4.5521 | 23658 | 507.1411 | 59.6223
4.5625 | 22068 | 500.7491 | 58.2353
4.5729 | 24127 | 495.1847 | 57.7369
4.5833 | 23345 | 485.5275 | 57.2504
4.5937 | 22595 | 486.0886 | 56.6056
4.6042 | 21580 | 481.8788 | 56.0848
4.6146 | 21228 | 472.8447 | 54.3665
4.625 | 21228 | 472.8447 | 54.3665
4.6354 | 21217 | 460.9522 | 53.2605
4.6458 | 20623 | 451.3532 | 52.65
4.6562 | 20848 | 444.3856 | 52.7577
4.6667 | 20232 | 437.5513 | 52.796
4.6771 | 19893 | 433.3707 | 52.3779
4.6875 | 19487 | 429.0556 | 52.4705
4.6979 | 18819 | 425.9849 | 53.2629
4.7083 | 18441 | 418.9673 | 52.7517
4.7187 | 18045 | 409.4605 | 51.5261
4.7292 | 17864 | 397.3387 | 49.6093
4.7396 | 17775 | 388.5326 | 48.9427
4.75 | 18608 | 380.7226 | 48.6296
4.7604 | 20969 | 375.8711 | 50.5147
4.7708 | 21559 | 387.657 | 52.3128
4.7812 | 20558 | 390.1003 | 53.6433
4.7917 | 19310 | 394.7099 | 53.6845
4.8021 | 17043 | 394.8389 | 50.9452
4.8125 | 17878 | 395.5286 | 52.9297
4.8229 | 21360 | 385.8824 | 52.9125
4.8333 | 22636 | 382.4531 | 53.4169
4.8437 | 22542 | 394.0581 | 56.0453
4.8542 | 24225 | 407.7909 | 58.8591
4.8646 | 20907 | 416.7992 | 59.5274
4.875 | 20907 | 416.7992 | 59.5274
4.8854 | 18809 | 431.2353 | 61.4901
4.8958 | 20576 | 431.3691 | 62.2881
4.9062 | 25680 | 424.2593 | 62.5216
4.9167 | 23444 | 425.1888 | 61.7995
4.9271 | 23139 | 442.605 | 62.9656
4.9375 | 23551 | 446.5288 | 63.1246
4.9479 | 20895 | 448.3036 | 62.498
4.9583 | 26044 | 450.6769 | 62.8879
4.9687 | 24830 | 442.8375 | 61.3545
4.9792 | 23966 | 454.1295 | 60.2793
4.9896 | 23311 | 458.0967 | 59.0631
5 | 22576 | 458.3102 | 58.0896
5.0104 | 20408 | 449.7551 | 56.5323
5.0208 | 18616 | 399.9887 | 54.3197
5.0312 | 18359 | 394.8652 | 54.6464
5.0417 | 18040 | 391.7643 | 56.0247
5.0521 | 17452 | 388.4417 | 57.8703
5.0625 | 17034 | 398.9005 | 61.3299
5.0729 | 16480 | 388.4907 | 60.7043
5.0833 | 15778 | 375.3283 | 58.7609
5.0937 | 15863 | 365.2611 | 57.7455
5.1042 | 15636 | 353.3523 | 54.773
5.1146 | 14246 | 341.7042 | 54.2506
5.125 | 14246 | 341.7042 | 54.2506
5.1354 | 13234 | 320.789 | 50.0168
5.1458 | 12513 | 308.9749 | 47.1829
5.1562 | 11946 | 292.4167 | 43.2167
5.1667 | 11373 | 276.7106 | 39.7989
5.1771 | 11968 | 266.7922 | 37.922
5.1875 | 11468 | 256.3913 | 36.0607
5.1979 | 11771 | 247.4693 | 33.6141
5.2083 | 12929 | 246.0487 | 33.8758
5.2187 | 12195 | 242.0051 | 33.7971
5.2292 | 13090 | 240.7754 | 33.8217
5.2396 | 13414 | 241.0834 | 33.7925
5.25 | 13404 | 240.4184 | 33.687
5.2604 | 12275 | 233.4367 | 33.0618
5.2708 | 11669 | 228.794 | 32.7299
5.2812 | 11895 | 225.7178 | 32.3323
5.2917 | 11705 | 222.5629 | 32.0183
5.3021 | 11843 | 220.6651 | 31.9139
5.3125 | 12189 | 220.0539 | 32.0175
5.3229 | 12669 | 220.9957 | 32.417
5.3333 | 12645 | 221.5555 | 32.8755
5.3437 | 12456 | 221.8627 | 33.2595
5.3542 | 13219 | 224.498 | 33.9222
5.3646 | 13732 | 229.2495 | 34.8031
5.375 | 13732 | 229.2495 | 34.8031
5.3854 | 16832 | 242.4853 | 38.5095
5.3958 | 16830 | 264.3305 | 45.1813
5.4062 | 21148 | 298.5998 | 52.554
5.4167 | 24560 | 337.0767 | 59.1388
5.4271 | 23953 | 375.3989 | 67.3838
5.4375 | 25904 | 413.6961 | 73.5202
5.4479 | 27488 | 452.3604 | 79.0333
5.4583 | 29553 | 486.992 | 82.3513
5.4687 | 29829 | 512.0381 | 83.1167
5.4792 | 29837 | 527.0739 | 80.2506
5.4896 | 29558 | 534.6193 | 75.3918
5.5 | 26139 | 530.6415 | 72.4019
5.5104 | 24925 | 514.1174 | 65.8659
5.5208 | 23924 | 503.5321 | 62.7521
5.5312 | 23857 | 496.7593 | 60.7403
5.5417 | 21088 | 482.346 | 58.3554
5.5521 | 24802 | 487.1721 | 58.6697
5.5625 | 24220 | 488.1851 | 57.8984
5.5729 | 22794 | 483.7227 | 56.8406
5.5833 | 21983 | 478.1815 | 56.5945
5.5937 | 19441 | 463.8046 | 54.8111
5.6042 | 17806 | 443.9218 | 53.3417
5.6146 | 23695 | 451.2177 | 53.5368
5.625 | 23695 | 451.2177 | 53.5368
5.6354 | 21662 | 445.7112 | 52.4682
5.6458 | 20152 | 436.3312 | 51.7294
5.6562 | 21161 | 433.8326 | 52.2112
5.6667 | 17348 | 417.8163 | 51.2607
5.6771 | 16651 | 402.0517 | 50.1672
5.6875 | 18264 | 397.5336 | 50.5418
5.6979 | 18220 | 394.7309 | 51.4456
5.7083 | 18613 | 392.3673 | 51.3013
5.7187 | 18056 | 386.3585 | 50.2523
5.7292 | 17578 | 376.4677 | 48.4223
5.7396 | 17335 | 368.1866 | 47.7673
5.75 | 17638 | 364.4546 | 47.6068
5.7604 | 17747 | 363.4811 | 49.4192
5.7708 | 17733 | 364.512 | 50.5312
5.7812 | 21738 | 376.5412 | 53.0298
5.7917 | 21176 | 383.8079 | 53.3209
5.8021 | 20749 | 388.1579 | 51.0733
5.8125 | 21158 | 398.1006 | 53.517
5.8229 | 17930 | 391.6764 | 52.7868
5.8333 | 19535 | 394.1391 | 53.6733
5.8437 | 22636 | 409.7801 | 56.9581
5.8542 | 21182 | 417.2129 | 58.9787
5.8646 | 21436 | 423.2762 | 59.968
5.875 | 21436 | 423.2762 | 59.968
5.8854 | 20522 | 426.0904 | 61.4483
5.8958 | 18098 | 420.0501 | 61.307
5.9062 | 24479 | 439.1413 | 63.2192
5.9167 | 22590 | 445.1918 | 62.8253
5.9271 | 21673 | 445.769 | 62.9284
5.9375 | 21063 | 443.6988 | 62.5903
5.9479 | 16683 | 424.9806 | 60.5834
5.9583 | 24122 | 438.8149 | 61.9038
5.9687 | 21831 | 438.9955 | 60.6811
5.9792 | 22589 | 440.2226 | 59.2644
5.9896 | 21074 | 435.9397 | 57.4484
6 | 18895 | 424.6631 | 55.6212
6.0104 | 16990 | 331.6601 | 49.5169
6.0208 | 15964 | 328.7477 | 50.0852
6.0312 | 15806 | 334.9662 | 51.0516
6.0417 | 15610 | 338.5293 | 52.819
6.0521 | 15247 | 345.2057 | 55.2486
6.0625 | 14989 | 351.7935 | 58.5205
6.0729 | 14647 | 338.5887 | 57.7894
6.0833 | 14212 | 326.6813 | 55.9646
6.0937 | 14266 | 317.3222 | 54.9879
6.1042 | 14126 | 305.7643 | 52.0524
6.1146 | 13264 | 298.6542 | 51.8564
6.125 | 13264 | 298.6542 | 51.8564
6.1354 | 12636 | 283.361 | 47.9766
6.1458 | 12189 | 276.6079 | 45.4481
6.1562 | 11836 | 264.1247 | 41.7228
6.1667 | 11481 | 253.2686 | 38.5838
6.1771 | 11851 | 244.3482 | 36.736
6.1875 | 11540 | 235.9743 | 34.9997
6.1979 | 11729 | 229.9633 | 32.694
6.2083 | 12450 | 225.8207 | 32.7715
6.2187 | 11994 | 223.2061 | 32.7946
6.2292 | 12552 | 220.6354 | 32.7174
6.2396 | 12755 | 219.7254 | 32.6135
6.25 | 12749 | 217.8284 | 32.4437
6.2604 | 12046 | 217.6297 | 32.2152
6.2708 | 11668 | 215.643 | 32.0419
6.2812 | 11810 | 214.1249 | 31.7186
6.2917 | 11692 | 213.9659 | 31.5665
6.3021 | 11778 | 214.6491 | 31.5945
6.3125 | 11994 | 213.7049 | 31.6718
6.3229 | 12294 | 213.4347 | 31.9941
6.3333 | 12280 | 213.2685 | 32.4142
6.3437 | 12162 | 213.1847 | 32.7838
6.3542 | 12640 | 215.238 | 33.394
6.3646 | 12962 | 217.1045 | 34.1071
6.375 | 12962 | 217.1045 | 34.1071
6.3854 | 14903 | 221.9973 | 37.2643
6.3958 | 14903 | 238.1265 | 43.6203
6.4062 | 17608 | 265.6808 | 50.4294
6.4167 | 19748 | 288.6647 | 55.9379
6.4271 | 19370 | 317.9179 | 63.6591
6.4375 | 20596 | 345.7851 | 69.0288
6.4479 | 21592 | 374.0344 | 73.7682
6.4583 | 22891 | 399.399 | 76.3136
6.4687 | 23068 | 416.2611 | 76.5079
6.4792 | 23077 | 424.1199 | 73.1623
6.4896 | 22905 | 426.8673 | 68.0025
6.5 | 20762 | 429.1195 | 65.6899
6.5104 | 20005 | 419.6784 | 59.6768
6.5208 | 19379 | 410.5991 | 56.7522
6.5312 | 19339 | 401.4863 | 54.6182
6.5417 | 17601 | 395.896 | 52.9966
6.5521 | 19939 | 391.3001 | 52.4411
6.5625 | 19576 | 384.9061 | 51.3064
6.5729 | 18681 | 385.2207 | 50.6582
6.5833 | 18173 | 384.0735 | 50.7412
6.5937 | 16574 | 381.3396 | 49.8416
6.6042 | 15545 | 376.1268 | 49.3228
6.6146 | 19259 | 368.5517 | 48.2172
6.625 | 19259 | 368.5517 | 48.2172
6.6354 | 17980 | 361.5032 | 47.2342
6.6458 | 17030 | 355.4402 | 46.8131
6.6562 | 17669 | 351.7595 | 47.1508
6.6667 | 15264 | 348.4523 | 47.2093
6.6771 | 14826 | 345.5327 | 46.873
6.6875 | 15846 | 343.8536 | 47.299
6.6979 | 15819 | 342.7469 | 48.3049
6.7083 | 16069 | 338.0813 | 48.0123
6.7187 | 15719 | 332.0825 | 47.0043
6.7292 | 15418 | 323.6957 | 45.2919
6.7396 | 15266 | 319.0726 | 44.8557
6.75 | 15459 | 316.9066 | 44.7646
6.7604 | 15531 | 327.2521 | 47.1876
6.7708 | 15524 | 332.832 | 48.5483
6.7812 | 18062 | 332.1753 | 50.1097
6.7917 | 17708 | 329.8909 | 49.8971
6.8021 | 17440 | 323.6499 | 47.0883
6.8125 | 17701 | 325.3296 | 49.0408
6.8229 | 15656 | 330.8984 | 49.1948
6.8333 | 16676 | 338.0192 | 50.2296
6.8437 | 18646 | 345.6661 | 52.8482
6.8542 | 17726 | 356.3269 | 55.141
6.8646 | 17889 | 356.7642 | 55.7966
6.875 | 17889 | 356.7642 | 55.7966
6.8854 | 17311 | 354.5723 | 57.066
6.8958 | 15773 | 357.4411 | 57.5921
6.9062 | 19830 | 369.3553 | 58.6288
6.9167 | 18631 | 372.8698 | 58.2234
6.9271 | 18051 | 374.18 | 58.434
6.9375 | 17665 | 375.6148 | 58.3352
6.9479 | 14880 | 370.4596 | 57.3949
6.9583 | 19617 | 376.8949 | 57.7698
6.9687 | 18161 | 378.5335 | 56.7891
6.9792 | 18646 | 376.0895 | 55.1058
6.9896 | 17683 | 373.5787 | 53.5013
7 | 16297 | 370.1972 | 52.2749
7.0104 | 15534 | 354.7521 | 50.6085
7.0208 | 15779 | 328.7487 | 50.0655
7.0312 | 18281 | 334.9662 | 51.322
7.0417 | 17472 | 338.5293 | 53.0234
7.0521 | 18215 | 345.2057 | 55.579
7.0625 | 18130 | 351.7935 | 58.8735
7.0729 | 13548 | 338.5887 | 57.6727
7.0833 | 13661 | 326.6813 | 55.9083
7.0937 | 13676 | 317.3222 | 54.9294
7.1042 | 13339 | 305.7643 | 51.977
7.1146 | 13075 | 298.6532 | 51.8388
7.125 | 13075 | 298.6532 | 51.8388
7.1354 | 12042 | 283.361 | 47.9233
7.1458 | 12042 | 276.6079 | 45.4355
7.1562 | 11397 | 264.1237 | 41.6864
7.1667 | 11220 | 253.2686 | 38.563
7.1771 | 10898 | 244.3472 | 36.663
7.1875 | 10627 | 235.9733 | 34.9325
7.1979 | 11347 | 229.9633 | 32.6665
7.2083 | 10876 | 225.8207 | 32.6614
7.2187 | 11186 | 223.2061 | 32.7391
7.2292 | 11343 | 220.6354 | 32.6356
7.2396 | 11624 | 219.7254 | 32.5377
7.25 | 11522 | 217.8284 | 32.3623
7.2604 | 12105 | 217.6297 | 32.2191
7.2708 | 11429 | 215.643 | 32.0262
7.2812 | 11457 | 214.1249 | 31.6958
7.2917 | 11826 | 213.9659 | 31.5752
7.3021 | 12021 | 214.6491 | 31.6103
7.3125 | 11488 | 213.7039 | 31.6392
7.3229 | 11613 | 213.4347 | 31.9504
7.3333 | 11632 | 213.2685 | 32.3728
7.3437 | 11482 | 213.1837 | 32.7405
7.3542 | 12270 | 215.2389 | 33.3703
7.3646 | 11978 | 217.1055 | 34.0437
7.375 | 11978 | 217.1055 | 34.0437
7.3854 | 11889 | 221.9973 | 37.07
7.3958 | 13692 | 238.1275 | 43.5396
7.4062 | 18050 | 265.6818 | 50.4621
7.4167 | 18506 | 288.6647 | 55.8381
7.4271 | 19118 | 317.9179 | 63.6372
7.4375 | 20560 | 345.7851 | 69.0254
7.4479 | 21862 | 374.0344 | 73.796
7.4583 | 23227 | 399.399 | 76.3514
7.4687 | 23379 | 416.2611 | 76.5453
7.4792 | 23258 | 424.1199 | 73.1852
7.4896 | 23272 | 426.8683 | 68.0511
7.5 | 23155 | 429.1205 | 66.0177
7.5104 | 20461 | 419.6774 | 59.74
7.5208 | 19774 | 410.6001 | 56.8065
7.5312 | 19390 | 401.4863 | 54.6251
7.5417 | 19166 | 395.896 | 53.2063
7.5521 | 18973 | 391.3001 | 52.3131
7.5625 | 18003 | 384.9061 | 51.1024
7.5729 | 19264 | 385.2207 | 50.7339
7.5833 | 18789 | 384.0735 | 50.8204
7.5937 | 18332 | 381.3396 | 50.0653
7.6042 | 17713 | 376.1268 | 49.5938
7.6146 | 17500 | 368.5517 | 48.0008
7.625 | 17500 | 368.5517 | 48.0008
7.6354 | 17495 | 361.5032 | 47.1754
7.6458 | 17134 | 355.4402 | 46.8255
7.6562 | 17273 | 351.7595 | 47.1041
7.6667 | 16898 | 348.4523 | 47.3997
7.6771 | 16692 | 345.5327 | 47.0874
7.6875 | 16445 | 343.8536 | 47.3668
7.6979 | 16037 | 342.7469 | 48.3291
7.7083 | 15806 | 338.0813 | 47.9836
7.7187 | 15565 | 332.0815 | 46.9879
7.7292 | 15456 | 323.6967 | 45.2959
7.7396 | 15402 | 319.0726 | 44.8699
7.75 | 15915 | 316.9066 | 44.8118
7.7604 | 17370 | 327.2521 | 47.3835
7.7708 | 17735 | 332.832 | 48.7867
7.7812 | 17121 | 332.1742 | 50.0082
7.7917 | 16355 | 329.8899 | 49.7523
7.8021 | 14962 | 323.6509 | 46.8301
7.8125 | 15477 | 325.3306 | 48.8117
7.8229 | 17623 | 330.8984 | 49.4017
7.8333 | 18411 | 338.0202 | 50.4167
7.8437 | 18356 | 345.6661 | 52.8164
7.8542 | 19395 | 356.3269 | 55.3293
7.8646 | 17352 | 356.7642 | 55.7363
7.875 | 17352 | 356.7642 | 55.7363
7.8854 | 16060 | 354.5723 | 56.9284
7.8958 | 17152 | 357.4401 | 57.744
7.9062 | 20304 | 369.3563 | 58.6834
7.9167 | 18926 | 372.8698 | 58.2577
7.9271 | 18740 | 374.18 | 58.5149
7.9375 | 18997 | 375.6148 | 58.4932
7.9479 | 17359 | 370.4596 | 57.6853
7.9583 | 20544 | 376.8959 | 57.8821
7.9687 | 19796 | 378.5335 | 56.9899
7.9792 | 19265 | 376.0906 | 55.1821
7.9896 | 18862 | 373.5797 | 53.6467
8 | 18409 | 370.1961 | 52.5341
8.0104 | 21474 | 405.8761 | 54.2133
8.0208 | 19620 | 399.9887 | 54.459
8.0312 | 19334 | 394.8652 | 54.7792
8.0417 | 18978 | 391.7643 | 56.1501
8.0521 | 18321 | 388.4407 | 57.984
8.0625 | 17855 | 398.9015 | 61.4396
8.0729 | 17237 | 388.4907 | 60.8017
8.0833 | 16453 | 375.3283 | 58.8446
8.0937 | 16548 | 365.2611 | 57.828
8.1042 | 16295 | 353.3523 | 54.8502
8.1146 | 14743 | 341.9295 | 54.3289
8.125 | 14743 | 341.9295 | 54.3289
8.1354 | 13613 | 320.789 | 50.0572
8.1458 | 12807 | 308.9749 | 47.2126
8.1562 | 12173 | 292.4167 | 43.2385
8.1667 | 11533 | 276.7106 | 39.8134
8.1771 | 12198 | 266.7912 | 37.9419
8.1875 | 11640 | 256.3903 | 36.0749
8.1979 | 11978 | 247.4693 | 33.6307
8.2083 | 13272 | 246.0487 | 33.9029
8.2187 | 12452 | 242.0061 | 33.817
8.2292 | 13453 | 240.7754 | 33.8495
8.2396 | 13815 | 241.0834 | 33.8232
8.25 | 13803 | 240.4174 | 33.7176
8.2604 | 12542 | 233.4357 | 33.0814
8.2708 | 11865 | 228.794 | 32.7439
8.2812 | 12118 | 225.7178 | 32.3479
8.2917 | 11906 | 222.5619 | 32.032
8.3021 | 12059 | 220.6651 | 31.9285
8.3125 | 12446 | 220.0539 | 32.0348
8.3229 | 12982 | 220.9957 | 32.4383
8.3333 | 12956 | 221.5555 | 32.8965
8.3437 | 12745 | 221.8627 | 33.279
8.3542 | 13597 | 224.4969 | 33.9482
8.3646 | 14171 | 229.2495 | 34.8338
8.375 | 14171 | 229.2495 | 34.8338
8.3854 | 17637 | 242.4853 | 38.5688
8.3958 | 17635 | 264.3305 | 45.2445
8.4062 | 22461 | 298.6008 | 52.6706
8.4167 | 26276 | 337.0767 | 59.3141
8.4271 | 25598 | 375.3989 | 67.5693
8.4375 | 27780 | 413.6961 | 73.7548
8.4479 | 29551 | 452.3604 | 79.3185
8.4583 | 31861 | 486.992 | 82.7013
8.4687 | 32171 | 512.0381 | 83.4993
8.4792 | 32180 | 527.0729 | 80.6565
8.4896 | 31869 | 534.6193 | 75.81
8.5 | 28047 | 530.6415 | 72.7503
8.5104 | 26690 | 514.1164 | 66.1859
8.5208 | 25572 | 503.5321 | 63.0469
8.5312 | 25496 | 496.7603 | 61.0328
8.5417 | 22401 | 482.346 | 58.5822
8.5521 | 26555 | 487.1721 | 58.9774
8.5625 | 25905 | 488.1841 | 58.195
8.5729 | 24310 | 483.7227 | 57.1044
8.5833 | 23404 | 478.1805 | 56.8374
8.5937 | 20560 | 463.8056 | 54.995
8.6042 | 18732 | 443.9218 | 53.4856
8.6146 | 25320 | 451.2177 | 53.7971
8.625 | 25320 | 451.2177 | 53.7971
8.6354 | 23046 | 445.7112 | 52.6887
8.6458 | 21357 | 436.3312 | 51.9174
8.6562 | 22487 | 433.8326 | 52.4168
8.6667 | 18221 | 417.8163 | 51.3897
8.6771 | 17442 | 402.0527 | 50.2781
8.6875 | 19246 | 397.5336 | 50.6766
8.6979 | 19197 | 394.7309 | 51.5771
8.7083 | 19637 | 392.3673 | 51.4381
8.7187 | 19014 | 386.3575 | 50.3783
8.7292 | 18480 | 376.4667 | 48.5387
8.7396 | 18208 | 368.1866 | 47.8773
8.75 | 18547 | 364.4546 | 47.7202
8.7604 | 18670 | 363.4811 | 49.5326
8.7708 | 18654 | 364.512 | 50.6437
8.7812 | 23137 | 376.5412 | 53.2088
8.7917 | 22509 | 383.8079 | 53.4958
8.8021 | 22031 | 388.1579 | 51.2442
8.8125 | 22489 | 398.1006 | 53.6977
8.8229 | 18876 | 391.6764 | 52.9122
8.8333 | 20674 | 394.1391 | 53.8248
8.8437 | 24145 | 409.7801 | 57.1672
8.8542 | 22518 | 417.2129 | 59.166
8.8646 | 22803 | 423.2762 | 60.1623
8.875 | 22803 | 423.2762 | 60.1623
8.8854 | 21780 | 426.0904 | 61.6272
8.8958 | 19067 | 420.0501 | 61.441
8.9062 | 26211 | 439.1423 | 63.4727
8.9167 | 24096 | 445.1928 | 63.0497
8.9271 | 23071 | 445.77 | 63.1375
8.9375 | 22388 | 443.6998 | 62.7881
8.9479 | 17483 | 424.9806 | 60.6968
8.9583 | 25814 | 438.8149 | 62.1559
8.9687 | 23248 | 438.9955 | 60.8938
8.9792 | 24098 | 440.2235 | 59.4942
8.9896 | 22402 | 435.9397 | 57.6494
9 | 19962 | 424.6631 | 55.7783
9.0104 | 18618 | 398.5001 | 53.4007
9.0208 | 19046 | 393.3037 | 54.0075
9.0312 | 23433 | 403.8392 | 55.8545
9.0417 | 22011 | 408.2183 | 57.4939
9.0521 | 23310 | 417.4127 | 60.3045
9.0625 | 23158 | 425.6805 | 63.6883
9.0729 | 15122 | 402.2217 | 61.2693
9.0833 | 15319 | 383.3403 | 59.1363
9.0937 | 15342 | 368.6021 | 57.8635
9.1042 | 14751 | 351.8203 | 54.5865
9.1146 | 14287 | 339.7802 | 54.1525
9.125 | 14287 | 339.7802 | 54.1525
9.1354 | 12478 | 319.354 | 49.8604
9.1458 | 12477 | 306.9709 | 47.074
9.1562 | 11347 | 288.3867 | 42.9496
9.1667 | 11037 | 272.1576 | 39.5317
9.1771 | 10473 | 258.0312 | 37.3391
9.1875 | 10000 | 244.7083 | 35.3368
9.1979 | 11258 | 236.1183 | 32.9808
9.2083 | 10436 | 228.5797 | 32.7737
9.2187 | 10976 | 223.7151 | 32.7521
9.2292 | 11250 | 219.4524 | 32.5682
9.2396 | 11740 | 217.5834 | 32.4339
9.25 | 11562 | 214.5434 | 32.1927
9.2604 | 12578 | 214.1457 | 32.0666
9.2708 | 11399 | 210.8371 | 31.773
9.2812 | 11448 | 208.3329 | 31.3923
9.2917 | 12090 | 208.1039 | 31.2846
9.3021 | 12429 | 209.0751 | 31.3436
9.3125 | 11500 | 207.2499 | 31.3023
9.3229 | 11717 | 206.5487 | 31.5964
9.3333 | 11751 | 206.0575 | 32.0027
9.3437 | 11489 | 205.3916 | 32.3337
9.3542 | 12859 | 208.553 | 33.0549
9.3646 | 12350 | 210.6715 | 33.7288
9.375 | 12350 | 210.6715 | 33.7288
9.3854 | 12194 | 215.6123 | 36.7541
9.3958 | 15329 | 235.4465 | 43.5038
9.4062 | 22901 | 274.7928 | 51.343
9.4167 | 23690 | 308.4187 | 57.3951
9.4271 | 24749 | 348.2379 | 65.8921
9.4375 | 27249 | 388.5991 | 72.1992
9.4479 | 29504 | 430.6684 | 78.0019
9.4583 | 31868 | 471.119 | 81.728
9.4687 | 32126 | 501.0931 | 82.8186
9.4792 | 31909 | 519.7029 | 80.1566
9.4896 | 31927 | 531.4913 | 75.6279
9.5 | 31719 | 540.9305 | 74.0525
9.5104 | 27039 | 534.3184 | 67.4458
9.5208 | 25844 | 522.5491 | 64.2126
9.5312 | 25174 | 510.6373 | 61.7853
9.5417 | 24783 | 502.4139 | 60.1624
9.5521 | 24444 | 495.2881 | 59.0782
9.5625 | 22762 | 484.3461 | 57.4217
9.5729 | 24940 | 484.5897 | 57.265
9.5833 | 24113 | 481.7965 | 57.1684
9.5937 | 23320 | 476.5376 | 56.182
9.6042 | 22247 | 467.7558 | 55.3934
9.6146 | 21875 | 456.8897 | 53.5688
9.625 | 21875 | 456.8897 | 53.5688
9.6354 | 21863 | 447.2112 | 52.5853
9.6458 | 21236 | 438.0462 | 51.995
9.6562 | 21473 | 432.2246 | 52.1678
9.6667 | 20822 | 426.1333 | 52.244
9.6771 | 20463 | 420.4427 | 51.7382
9.6875 | 20034 | 415.8836 | 51.8146
9.6979 | 19328 | 411.4279 | 52.5267
9.7083 | 18928 | 403.5123 | 51.9631
9.7187 | 18510 | 394.2915 | 50.7516
9.7292 | 18319 | 383.0207 | 48.8803
9.7396 | 18224 | 375.8796 | 48.3045
9.75 | 19106 | 372.8276 | 48.2564
9.7604 | 21604 | 388.2901 | 51.3019
9.7708 | 22228 | 395.84 | 52.869
9.7812 | 21169 | 395.2933 | 54.0189
9.7917 | 19849 | 391.4279 | 53.5743
9.8021 | 17451 | 380.7979 | 50.2302
9.8125 | 18335 | 380.4816 | 52.158
9.8229 | 22018 | 389.4494 | 53.2013
9.8333 | 23369 | 400.7131 | 54.563
9.8437 | 23270 | 411.3441 | 57.1361
9.8542 | 25050 | 426.9039 | 60.0863
9.8646 | 21540 | 426.3132 | 60.1561
9.875 | 21540 | 426.3132 | 60.1561
9.8854 | 19321 | 420.6094 | 60.9717
9.8958 | 21190 | 423.6741 | 61.9397
9.9062 | 26591 | 443.1753 | 63.7658
9.9167 | 24225 | 448.8688 | 63.2819
9.9271 | 23902 | 451.657 | 63.6021
9.9375 | 24339 | 455.0398 | 63.7372
9.9479 | 21529 | 447.4716 | 62.5475
9.9583 | 26978 | 460.1359 | 63.5916
9.9687 | 25693 | 464.3935 | 62.7504
9.9792 | 24779 | 462.8136 | 60.9135
9.9896 | 24086 | 460.1727 | 59.3084
10 | 23308 | 455.7101 | 58.0596
10.0104 | 21014 | 433.3151 | 55.7004
10.0208 | 19118 | 405.8737 | 54.7168
10.0312 | 18847 | 406.2652 | 55.3458
10.0417 | 18509 | 402.7483 | 56.6962
10.0521 | 17886 | 400.4607 | 58.5891
10.0625 | 17445 | 399.2405 | 61.4037
10.0729 | 16858 | 392.9787 | 60.9977
10.0833 | 16116 | 396.4353 | 59.9493
10.0937 | 16206 | 383.4361 | 58.775
10.1042 | 15965 | 368.3253 | 55.6244
10.1146 | 14494 | 359.9292 | 55.2555
10.125 | 14494 | 359.9292 | 55.2555
10.1354 | 13423 | 344.187 | 51.2796
10.1458 | 12660 | 333.8499 | 48.5108
10.1562 | 12059 | 317.0577 | 44.5214
10.1667 | 11453 | 300.8306 | 41.0666
10.1771 | 12083 | 286.6642 | 38.9758
10.1875 | 11554 | 272.8983 | 36.9315
10.1979 | 11875 | 262.4013 | 34.405
10.2083 | 13101 | 254.1727 | 34.3194
10.2187 | 12323 | 248.2211 | 34.1346
10.2292 | 13271 | 246.1034 | 34.118
10.2396 | 13614 | 242.0434 | 33.8589
10.25 | 13604 | 240.7554 | 33.7206
10.2604 | 12408 | 240.4567 | 33.4415
10.2708 | 11767 | 236.2431 | 33.1271
10.2812 | 12006 | 233.0128 | 32.7229
10.2917 | 11805 | 228.5169 | 32.3364
10.3021 | 11951 | 225.9311 | 32.1976
10.3125 | 12317 | 223.0869 | 32.1857
10.3229 | 12825 | 221.2077 | 32.4389
10.3333 | 12800 | 220.6275 | 32.8368
10.3437 | 12600 | 221.9566 | 33.2747
10.3542 | 13408 | 222.8049 | 33.845
10.3646 | 13952 | 223.9355 | 34.5356
10.375 | 13952 | 223.9355 | 34.5356
10.3854 | 17235 | 230.8373 | 37.9001
10.3958 | 17233 | 245.1775 | 44.1624
10.4062 | 21804 | 265.1568 | 50.7095
10.4167 | 25418 | 284.4257 | 56.145
10.4271 | 24776 | 322.0049 | 64.367
10.4375 | 26842 | 362.7951 | 70.6261
10.4479 | 28519 | 395.6424 | 75.7771
10.4583 | 30707 | 427.852 | 78.9243
10.4687 | 31000 | 456.0231 | 79.8884
10.4792 | 31009 | 478.9799 | 77.5175
10.4896 | 30713 | 495.3973 | 73.2112
10.5 | 27093 | 509.6345 | 71.3304
10.5104 | 25808 | 516.9674 | 66.1931
10.5208 | 24748 | 510.4691 | 63.3037
10.5312 | 24677 | 503.0543 | 61.2522
10.5417 | 21745 | 495.8899 | 59.239
10.5521 | 25678 | 493.2741 | 59.1811
10.5625 | 25062 | 480.6961 | 57.6101
10.5729 | 23552 | 487.0767 | 57.1669
10.5833 | 22693 | 489.3655 | 57.3575
10.5937 | 20001 | 485.2256 | 56.1043
10.6042 | 18269 | 478.2708 | 55.3134
10.6146 | 24508 | 460.1237 | 54.1847
10.625 | 24508 | 460.1237 | 54.1847
10.6354 | 22354 | 437.1342 | 52.0876
10.6458 | 20755 | 445.6882 | 52.3517
10.6562 | 21824 | 442.8895 | 52.8289
10.6667 | 17785 | 435.8393 | 52.3177
10.6771 | 17047 | 434.9827 | 52.0261
10.6875 | 18755 | 420.7456 | 51.8986
10.6979 | 18708 | 407.6079 | 52.2271
10.7083 | 19125 | 400.6303 | 51.8303
10.7187 | 18535 | 392.7755 | 50.6708
10.7292 | 18029 | 386.2027 | 49.018
10.7396 | 17772 | 380.6086 | 48.5057
10.75 | 18093 | 374.1766 | 48.2
10.7604 | 18209 | 367.5061 | 49.6982
10.7708 | 18193 | 368.129 | 50.7874
10.7812 | 22437 | 365.3062 | 52.4771
10.7917 | 21842 | 363.4009 | 52.2469
10.8021 | 21390 | 376.1009 | 50.4752
10.8125 | 21824 | 387.9146 | 53.0275
10.8229 | 18403 | 393.2404 | 52.9362
10.8333 | 20104 | 400.0661 | 54.082
10.8437 | 23390 | 396.2871 | 56.2854
10.8542 | 21850 | 401.2219 | 58.1622
10.8646 | 22120 | 415.2362 | 59.6067
10.875 | 22120 | 415.2362 | 59.6067
10.8854 | 21151 | 421.5534 | 61.2805
10.8958 | 18582 | 428.3361 | 61.8339
10.9062 | 25345 | 429.7403 | 62.7953
10.9167 | 23343 | 421.5688 | 61.576
10.9271 | 22372 | 438.576 | 62.6222
10.9375 | 21725 | 442.8588 | 62.641
10.9479 | 17083 | 442.4236 | 61.5958
10.9583 | 24968 | 439.3459 | 62.0609
10.9687 | 22540 | 420.3625 | 59.7205
10.9792 | 23343 | 432.8236 | 58.9533
10.9896 | 21738 | 432.7157 | 57.3657
11 | 19429 | 435.7362 | 56.3188
11.0104 | 18156 | 418.7301 | 54.4544
11.0208 | 18561 | 406.6767 | 54.6824
11.0312 | 22713 | 398.8902 | 55.4699
11.0417 | 21366 | 396.0663 | 56.7138
11.0521 | 22596 | 409.4287 | 59.7438
11.0625 | 22452 | 415.6835 | 63.0135
11.0729 | 14847 | 421.9307 | 62.2922
11.0833 | 15033 | 423.1963 | 61.2461
11.0937 | 15055 | 397.1581 | 59.3662
11.1042 | 14496 | 376.3303 | 55.8715
11.1146 | 14056 | 363.2672 | 55.3816
11.125 | 14056 | 363.2672 | 55.3816
11.1354 | 12345 | 342.654 | 51.0731
11.1458 | 12344 | 331.9259 | 48.3744
11.1562 | 11274 | 315.6217 | 44.3627
11.1667 | 10981 | 298.8276 | 40.915
11.1771 | 10448 | 282.6362 | 38.6115
11.1875 | 10000 | 268.3473 | 36.5567
11.1979 | 11190 | 253.6453 | 33.8895
11.2083 | 10412 | 242.4967 | 33.4925
11.2187 | 10923 | 236.8771 | 33.4322
11.2292 | 11182 | 228.6434 | 33.0422
11.2396 | 11646 | 223.7624 | 32.7508
11.25 | 11478 | 219.4434 | 32.4442
11.2604 | 12439 | 214.5957 | 32.0814
11.2708 | 11323 | 213.56 | 31.91
11.2812 | 11370 | 213.7329 | 31.6694
11.2917 | 11977 | 210.5689 | 31.4074
11.3021 | 12298 | 208.5541 | 31.3076
11.3125 | 11419 | 208.6369 | 31.3696
11.3229 | 11624 | 209.6226 | 31.751
11.3333 | 11656 | 207.8295 | 32.0901
11.3437 | 11409 | 207.5177 | 32.4399
11.3542 | 12704 | 207.3159 | 32.9796
11.3646 | 12223 | 207.4735 | 33.553
11.375 | 12223 | 207.4735 | 33.553
11.3854 | 12076 | 214.9023 | 36.7102
11.3958 | 15040 | 226.6095 | 43.0091
11.4062 | 22202 | 238.2968 | 49.2052
11.4167 | 22948 | 255.5587 | 54.2938
11.4271 | 23950 | 298.2109 | 62.9163
11.4375 | 26314 | 334.1531 | 68.8839
11.4479 | 28447 | 368.4974 | 74.1426
11.4583 | 30682 | 402.767 | 77.3936
11.4687 | 30926 | 434.3411 | 78.5554
11.4792 | 30720 | 463.1119 | 76.5077
11.4896 | 30737 | 484.4543 | 72.5487
11.5 | 30540 | 502.2645 | 71.479
11.5104 | 26113 | 527.2454 | 66.8543
11.5208 | 24983 | 533.0601 | 64.6641
11.5312 | 24349 | 523.2403 | 62.3649
11.5417 | 23979 | 514.893 | 60.7385
11.5521 | 23658 | 507.1411 | 59.6223
11.5625 | 22068 | 500.7491 | 58.2353
11.5729 | 24127 | 495.1847 | 57.7369
11.5833 | 23345 | 485.5275 | 57.2504
11.5937 | 22595 | 486.0886 | 56.6056
11.6042 | 21580 | 481.8788 | 56.0848
11.6146 | 21228 | 472.8447 | 54.3665
11.625 | 21228 | 472.8447 | 54.3665
11.6354 | 21217 | 460.9522 | 53.2605
11.6458 | 20623 | 451.3532 | 52.65
11.6562 | 20848 | 444.3856 | 52.7577
11.6667 | 20232 | 437.5513 | 52.796
11.6771 | 19893 | 433.3707 | 52.3779
11.6875 | 19487 | 429.0556 | 52.4705
11.6979 | 18819 | 425.9849 | 53.2629
11.7083 | 18441 | 418.9673 | 52.7517
11.7187 | 18045 | 409.4605 | 51.5261
11.7292 | 17864 | 397.3387 | 49.6093
11.7396 | 17775 | 388.5326 | 48.9427
11.75 | 18608 | 380.7226 | 48.6296
11.7604 | 20969 | 375.8711 | 50.5147
11.7708 | 21559 | 387.657 | 52.3128
11.7812 | 20558 | 390.1003 | 53.6433
11.7917 | 19310 | 394.7099 | 53.6845
11.8021 | 17043 | 394.8389 | 50.9452
11.8125 | 17878 | 395.5286 | 52.9297
11.8229 | 21360 | 385.8824 | 52.9125
11.8333 | 22636 | 382.4531 | 53.4169
11.8437 | 22542 | 394.0581 | 56.0453
11.8542 | 24225 | 407.7909 | 58.8591
11.8646 | 20907 | 416.7992 | 59.5274
11.875 | 20907 | 416.7992 | 59.5274
11.8854 | 18809 | 431.2353 | 61.4901
11.8958 | 20576 | 431.3691 | 62.2881
11.9062 | 25680 | 424.2593 | 62.5216
11.9167 | 23444 | 425.1888 | 61.7995
11.9271 | 23139 | 442.605 | 62.9656
11.9375 | 23551 | 446.5288 | 63.1246
11.9479 | 20895 | 448.3036 | 62.498
11.9583 | 26044 | 450.6769 | 62.8879
11.9687 | 24830 | 442.8375 | 61.3545
11.9792 | 23966 | 454.1295 | 60.2793
11.9896 | 23311 | 458.0967 | 59.0631
12 | 22576 | 458.3102 | 58.0896
12.0104 | 20408 | 449.7551 | 56.5323
12.0208 | 18616 | 399.9887 | 54.3197
12.0312 | 18359 | 394.8652 | 54.6464
12.0417 | 18040 | 391.7643 | 56.0247
12.0521 | 17452 | 388.4417 | 57.8703
12.0625 | 17034 | 398.9005 | 61.3299
12.0729 | 16480 | 388.4907 | 60.7043
12.0833 | 15778 | 375.3283 | 58.7609
12.0937 | 15863 | 365.2611 | 57.7455
12.1042 | 15636 | 353.3523 | 54.773
12.1146 | 14246 | 341.7042 | 54.2506
12.125 | 14246 | 341.7042 | 54.2506
12.1354 | 13234 | 320.789 | 50.0168
12.1458 | 12513 | 308.9749 | 47.1829
12.1562 | 11946 | 292.4167 | 43.2167
12.1667 | 11373 | 276.7106 | 39.7989
12.1771 | 11968 | 266.7922 | 37.922
12.1875 | 11468 | 256.3913 | 36.0607
12.1979 | 11771 | 247.4693 | 33.6141
12.2083 | 12929 | 246.0487 | 33.8758
12.2187 | 12195 | 242.0051 | 33.7971
12.2292 | 13090 | 240.7754 | 33.8217
12.2396 | 13414 | 241.0834 | 33.7925
12.25 | 13404 | 240.4184 | 33.687
12.2604 | 12275 | 233.4367 | 33.0618
12.2708 | 11669 | 228.794 | 32.7299
12.2812 | 11895 | 225.7178 | 32.3323
12.2917 | 11705 | 222.5629 | 32.0183
12.3021 | 11843 | 220.6651 | 31.9139
12.3125 | 12189 | 220.0539 | 32.0175
12.3229 | 12669 | 220.9957 | 32.417
12.3333 | 12645 | 221.5555 | 32.8755
12.3437 | 12456 | 221.8627 | 33.2595
12.3542 | 13219 | 224.498 | 33.9222
12.3646 | 13732 | 229.2495 | 34.8031
12.375 | 13732 | 229.2495 | 34.8031
12.3854 | 16832 | 242.4853 | 38.5095
12.3958 | 16830 | 264.3305 | 45.1813
12.4062 | 21148 | 298.5998 | 52.554
12.4167 | 24560 | 337.0767 | 59.1388
12.4271 | 23953 | 375.3989 | 67.3838
12.4375 | 25904 | 413.6961 | 73.5202
12.4479 | 27488 | 452.3604 | 79.0333
12.4583 | 29553 | 486.992 | 82.3513
12.4687 | 29829 | 512.0381 | 83.1167
12.4792 | 29837 | 527.0739 | 80.2506
12.4896 | 29558 | 534.6193 | 75.3918
12.5 | 26139 | 530.6415 | 72.4019
12.5104 | 24925 | 514.1174 | 65.8659
12.5208 | 23924 | 503.5321 | 62.7521
12.5312 | 23857 | 496.7593 | 60.7403
12.5417 | 21088 | 482.346 | 58.3554
12.5521 | 24802 | 487.1721 | 58.6697
12.5625 | 24220 | 488.1851 | 57.8984
12.5729 | 22794 | 483.7227 | 56.8406
12.5833 | 21983 | 478.1815 | 56.5945
12.5937 | 19441 | 463.8046 | 54.8111
12.6042 | 17806 | 443.9218 | 53.3417
12.6146 | 23695 | 451.2177 | 53.5368
12.625 | 23695 | 451.2177 | 53.5368
12.6354 | 21662 | 445.7112 | 52.4682
12.6458 | 20152 | 436.3312 | 51.7294
12.6562 | 21161 | 433.8326 | 52.2112
12.6667 | 17348 | 417.8163 | 51.2607
12.6771 | 16651 | 402.0517 | 50.1672
12.6875 | 18264 | 397.5336 | 50.5418
12.6979 | 18220 | 394.7309 | 51.4456
12.7083 | 18613 | 392.3673 | 51.3013
12.7187 | 18056 | 386.3585 | 50.2523
12.7292 | 17578 | 376.4677 | 48.4223
12.7396 | 17335 | 368.1866 | 47.7673
12.75 | 17638 | 364.4546 | 47.6068
12.7604 | 17747 | 363.4811 | 49.4192
12.7708 | 17733 | 364.512 | 50.5312
12.7812 | 21738 | 376.5412 | 53.0298
12.7917 | 21176 | 383.8079 | 53.3209
12.8021 | 20749 | 388.1579 | 51.0733
12.8125 | 21158 | 398.1006 | 53.517
12.8229 | 17930 | 391.6764 | 52.7868
12.8333 | 19535 | 394.1391 | 53.6733
12.8437 | 22636 | 409.7801 | 56.9581
12.8542 | 21182 | 417.2129 | 58.9787
12.8646 | 21436 | 423.2762 | 59.968
12.875 | 21436 | 423.2762 | 59.968
12.8854 | 20522 | 426.0904 | 61.4483
12.8958 | 18098 | 420.0501 | 61.307
12.9062 | 24479 | 439.1413 | 63.2192
12.9167 | 22590 | 445.1918 | 62.8253
12.9271 | 21673 | 445.769 | 62.9284
12.9375 | 21063 | 443.6988 | 62.5903
12.9479 | 16683 | 424.9806 | 60.5834
12.9583 | 24122 | 438.8149 | 61.9038
12.9687 | 21831 | 438.9955 | 60.6811
12.9792 | 22589 | 440.2226 | 59.2644
12.9896 | 21074 | 435.9397 | 57.4484
13 | 18895 | 424.6631 | 55.6212
13.0104 | 16990 | 331.6601 | 49.5169
13.0208 | 15964 | 328.7477 | 50.0852
13.0312 | 15806 | 334.9662 | 51.0516
13.0417 | 15610 | 338.5293 | 52.819
13.0521 | 15247 | 345.2057 | 55.2486
13.0625 | 14989 | 351.7935 | 58.5205
13.0729 | 14647 | 338.5887 | 57.7894
13.0833 | 14212 | 326.6813 | 55.9646
13.0937 | 14266 | 317.3222 | 54.9879
13.1042 | 14126 | 305.7643 | 52.0524
13.1146 | 13264 | 298.6542 | 51.8564
13.125 | 13264 | 298.6542 | 51.8564
13.1354 | 12636 | 283.361 | 47.9766
13.1458 | 12189 | 276.6079 | 45.4481
13.1562 | 11836 | 264.1247 | 41.7228
13.1667 | 11481 | 253.2686 | 38.5838
13.1771 | 11851 | 244.3482 | 36.736
13.1875 | 11540 | 235.9743 | 34.9997
13.1979 | 11729 | 229.9633 | 32.694
13.2083 | 12450 | 225.8207 | 32.7715
13.2187 | 11994 | 223.2061 | 32.7946
13.2292 | 12552 | 220.6354 | 32.7174
13.2396 | 12755 | 219.7254 | 32.6135
13.25 | 12749 | 217.8284 | 32.4437
13.2604 | 12046 | 217.6297 | 32.2152
13.2708 | 11668 | 215.643 | 32.0419
13.2812 | 11810 | 214.1249 | 31.7186
13.2917 | 11692 | 213.9659 | 31.5665
13.3021 | 11778 | 214.6491 | 31.5945
13.3125 | 11994 | 213.7049 | 31.6718
13.3229 | 12294 | 213.4347 | 31.9941
13.3333 | 12280 | 213.2685 | 32.4142
13.3437 | 12162 | 213.1847 | 32.7838
13.3542 | 12640 | 215.238 | 33.394
13.3646 | 12962 | 217.1045 | 34.1071
13.375 | 12962 | 217.1045 | 34.1071
13.3854 | 14903 | 221.9973 | 37.2643
13.3958 | 14903 | 238.1265 | 43.6203
13.4062 | 17608 | 265.6808 | 50.4294
13.4167 | 19748 | 288.6647 | 55.9379
13.4271 | 19370 | 317.9179 | 63.6591
13.4375 | 20596 | 345.7851 | 69.0288
13.4479 | 21592 | 374.0344 | 73.7682
13.4583 | 22891 | 399.399 | 76.3136
13.4687 | 23068 | 416.2611 | 76.5079
13.4792 | 23077 | 424.1199 | 73.1623
13.4896 | 22905 | 426.8673 | 68.0025
13.5 | 20762 | 429.1195 | 65.6899
13.5104 | 20005 | 419.6784 | 59.6768
13.5208 | 19379 | 410.5991 | 56.7522
13.5312 | 19339 | 401.4863 | 54.6182
13.5417 | 17601 | 395.896 | 52.9966
13.5521 | 19939 | 391.3001 | 52.4411
13.5625 | 19576 | 384.9061 | 51.3064
13.5729 | 18681 | 385.2207 | 50.6582
13.5833 | 18173 | 384.0735 | 50.7412
13.5937 | 16574 | 381.3396 | 49.8416
13.6042 | 15545 | 376.1268 | 49.3228
13.6146 | 19259 | 368.5517 | 48.2172
13.625 | 19259 | 368.5517 | 48.2172
13.6354 | 17980 | 361.5032 | 47.2342
13.6458 | 17030 | 355.4402 | 46.8131
13.6562 | 17669 | 351.7595 | 47.1508
13.6667 | 15264 | 348.4523 | 47.2093
13.6771 | 14826 | 345.5327 | 46.873
13.6875 | 15846 | 343.8536 | 47.299
13.6979 | 15819 | 342.7469 | 48.3049
13.7083 | 16069 | 338.0813 | 48.0123
13.7187 | 15719 | 332.0825 | 47.0043
13.7292 | 15418 | 323.6957 | 45.2919
13.7396 | 15266 | 319.0726 | 44.8557
13.75 | 15459 | 316.9066 | 44.7646
13.7604 | 15531 | 327.2521 | 47.1876
13.7708 | 15524 | 332.832 | 48.5483
13.7812 | 18062 | 332.1753 | 50.1097
13.7917 | 17708 | 329.8909 | 49.8971
13.8021 | 17440 | 323.6499 | 47.0883
13.8125 | 17701 | 325.3296 | 49.0408
13.8229 | 15656 | 330.8984 | 49.1948
13.8333 | 16676 | 338.0192 | 50.2296
13.8437 | 18646 | 345.6661 | 52.8482
13.8542 | 17726 | 356.3269 | 55.141
13.8646 | 17889 | 356.7642 | 55.7966
13.875 | 17889 | 356.7642 | 55.7966
13.8854 | 17311 | 354.5723 | 57.066
13.8958 | 15773 | 357.4411 | 57.5921
13.9062 | 19830 | 369.3553 | 58.6288
13.9167 | 18631 | 372.8698 | 58.2234
13.9271 | 18051 | 374.18 | 58.434
13.9375 | 17665 | 375.6148 | 58.3352
13.9479 | 14880 | 370.4596 | 57.3949
13.9583 | 19617 | 376.8949 | 57.7698
13.9687 | 18161 | 378.5335 | 56.7891
13.9792 | 18646 | 376.0895 | 55.1058
13.9896 | 17683 | 373.5787 | 53.5013
14 | 16297 | 370.1972 | 52.2749
14.0104 | 15534 | 354.7521 | 50.6085
14.0104 | 15534 | 354.7521 | 50.6085

## CSTR5
Unit overview
Name: | CSTR5
Sumo name: | CSTR6_1_3
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and calculated DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1333 | m3
htank | Tank depth | 4 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 15000 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 1
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XPAO_0 | Phosphorus accumulating organisms (PAO) initial concentration | 370 | g COD/m3
XGAO_0 | Glycogen accumulating organisms (GAO) initial concentration | 370 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 222 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SO2_0 | Dissolved oxygen (O2) initial concentration | 2 | g O2/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XAlOH_0 | Aluminium hydroxide compounds (AlOH) initial concentration | 1e-40 | g Al/m3
XAlP_0 | Aluminium phosphate compounds (AlP) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration | 0.054 | g TIC/m3
GCH4,aer | Methane gas (CH4) off-gas concentration | 0.001 | g COD/m3
GH2,aer | Hydrogen gas (H2) off-gas concentration | 0.05 | g COD/m3
GO2,aer | Oxygen gas (O2) off-gas concentration | 1.3 | g O2/m3
GNH3,aer | Ammonia gas (NH3) off-gas concentration | 1e-40 | g N/m3
GN2,aer | Nitrogen gas (N2) off-gas concentration | 4.9 | g N/m3
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 0.11359 | g TIC/m3
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 1.3734 | g N/m3
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | g O2/m3
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | g N/m3
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble | Bubble Sauter mean diameter | 0.003 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
ngas,dry,limit | Gas phase molar concentration limit | 1e-05
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the grapchics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.

## CSTR4
Unit overview
Name: | CSTR4
Sumo name: | CSTR6_1_2
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and calculated DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1333 | m3
htank | Tank depth | 4 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 50000 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 1
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XPAO_0 | Phosphorus accumulating organisms (PAO) initial concentration | 370 | g COD/m3
XGAO_0 | Glycogen accumulating organisms (GAO) initial concentration | 370 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 222 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SO2_0 | Dissolved oxygen (O2) initial concentration | 2 | g O2/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XAlOH_0 | Aluminium hydroxide compounds (AlOH) initial concentration | 1e-40 | g Al/m3
XAlP_0 | Aluminium phosphate compounds (AlP) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration | 0.054 | g TIC/m3
GCH4,aer | Methane gas (CH4) off-gas concentration | 0.001 | g COD/m3
GH2,aer | Hydrogen gas (H2) off-gas concentration | 0.05 | g COD/m3
GO2,aer | Oxygen gas (O2) off-gas concentration | 1.3 | g O2/m3
GNH3,aer | Ammonia gas (NH3) off-gas concentration | 1e-40 | g N/m3
GN2,aer | Nitrogen gas (N2) off-gas concentration | 4.9 | g N/m3
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 0.11359 | g TIC/m3
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 1.3734 | g N/m3
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | g O2/m3
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | g N/m3
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble | Bubble Sauter mean diameter | 0.003 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
ngas,dry,limit | Gas phase molar concentration limit | 1e-05
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the grapchics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.

## CSTR3
Unit overview
Name: | CSTR3
Sumo name: | CSTR6_1_1
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and calculated DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1333 | m3
htank | Tank depth | 4 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 50000 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 1
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XPAO_0 | Phosphorus accumulating organisms (PAO) initial concentration | 370 | g COD/m3
XGAO_0 | Glycogen accumulating organisms (GAO) initial concentration | 370 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 222 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SO2_0 | Dissolved oxygen (O2) initial concentration | 2 | g O2/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XAlOH_0 | Aluminium hydroxide compounds (AlOH) initial concentration | 1e-40 | g Al/m3
XAlP_0 | Aluminium phosphate compounds (AlP) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration | 0.054 | g TIC/m3
GCH4,aer | Methane gas (CH4) off-gas concentration | 0.001 | g COD/m3
GH2,aer | Hydrogen gas (H2) off-gas concentration | 0.05 | g COD/m3
GO2,aer | Oxygen gas (O2) off-gas concentration | 1.3 | g O2/m3
GNH3,aer | Ammonia gas (NH3) off-gas concentration | 1e-40 | g N/m3
GN2,aer | Nitrogen gas (N2) off-gas concentration | 4.9 | g N/m3
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 0.11359 | g TIC/m3
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 1.3734 | g N/m3
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | g O2/m3
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | g N/m3
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble | Bubble Sauter mean diameter | 0.003 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
ngas,dry,limit | Gas phase molar concentration limit | 1e-05
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the grapchics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.

## CSTR2
Unit overview
Name: | CSTR2
Sumo name: | CSTR6_1
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and calculated DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1000 | m3
htank | Tank depth | 4 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 0 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 0.7
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XPAO_0 | Phosphorus accumulating organisms (PAO) initial concentration | 370 | g COD/m3
XGAO_0 | Glycogen accumulating organisms (GAO) initial concentration | 370 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 222 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SO2_0 | Dissolved oxygen (O2) initial concentration | 2 | g O2/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XAlOH_0 | Aluminium hydroxide compounds (AlOH) initial concentration | 1e-40 | g Al/m3
XAlP_0 | Aluminium phosphate compounds (AlP) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration | 0.054 | g TIC/m3
GCH4,aer | Methane gas (CH4) off-gas concentration | 0.001 | g COD/m3
GH2,aer | Hydrogen gas (H2) off-gas concentration | 0.05 | g COD/m3
GO2,aer | Oxygen gas (O2) off-gas concentration | 1.3 | g O2/m3
GNH3,aer | Ammonia gas (NH3) off-gas concentration | 1e-40 | g N/m3
GN2,aer | Nitrogen gas (N2) off-gas concentration | 4.9 | g N/m3
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 0.11359 | g TIC/m3
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 1.3734 | g N/m3
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | g O2/m3
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | g N/m3
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble | Bubble Sauter mean diameter | 0.003 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
ngas,dry,limit | Gas phase molar concentration limit | 1e-05
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the grapchics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.

## CSTR1
Unit overview
Name: | CSTR1
Sumo name: | CSTR6
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and calculated DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.V | Volume | 1000 | m3
htank | Tank depth | 4 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
Qair,N | Air flow | 0 | Nm3 gas.d-1
α | Alpha (process water/clean water) factor | 0.7
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XPAO_0 | Phosphorus accumulating organisms (PAO) initial concentration | 370 | g COD/m3
XGAO_0 | Glycogen accumulating organisms (GAO) initial concentration | 370 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 222 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SO2_0 | Dissolved oxygen (O2) initial concentration | 2 | g O2/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XAlOH_0 | Aluminium hydroxide compounds (AlOH) initial concentration | 1e-40 | g Al/m3
XAlP_0 | Aluminium phosphate compounds (AlP) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration | 0.054 | g TIC/m3
GCH4,aer | Methane gas (CH4) off-gas concentration | 0.001 | g COD/m3
GH2,aer | Hydrogen gas (H2) off-gas concentration | 0.05 | g COD/m3
GO2,aer | Oxygen gas (O2) off-gas concentration | 1.3 | g O2/m3
GNH3,aer | Ammonia gas (NH3) off-gas concentration | 1e-40 | g N/m3
GN2,aer | Nitrogen gas (N2) off-gas concentration | 4.9 | g N/m3
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 0.11359 | g TIC/m3
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 1.3734 | g N/m3
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 1e-40 | g COD/m3
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | g O2/m3
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | g N/m3
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble | Bubble Sauter mean diameter | 0.003 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
ngas,dry,limit | Gas phase molar concentration limit | 1e-05
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the grapchics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.

## Clarifier
Unit overview
Name: | Clarifier
Sumo name: | Clarifier2
Category: | Separators
Unit: | Clarifier
Type: | 1D layered clarifier with triple exponential settling velocity model
Settings
Clarifier settings
Symbol | Name | Value | Unit | Comment
A | Surface area | 1500 | m2
haverage | Depth | 4 | m
Qsludge,target | Sludge flow | 18831 | m3/d
hinp | Depth of influent layer from top | 2 | m
Settling parameters
Symbol | Name | Value | Unit | Comment
vmax | Maximum Vesilind settling velocity | 474 | m/d
rhin | Coefficient for hindered settling | 0.576 | L/g
rfloc | Coefficient for flocculent settling | 2.86 | L/g
fns | Fraction of non-settleable solids | 0.228 | %
vbnd | Boundary settling velocity | 270 | m/d
rcompr | Coefficient for compression | 0.5 | L/g
compron | Boundary compression concentration | 6000 | g/m3 | Compression is taken into account above this value
XTSS,min,max | Non-settleable TSS | 20 | g/m3
XTSS,min,blanket | Concentration at top of sludge blanket | 2500 | g/m3
Layer number
Symbol | Name | Value | Unit | Comment
n | Number of layers | 10
Layered clarifier parameters
Symbol | Name | Value | Unit | Comment
efffQ[] | Fraction of effluent flow from the layers | {100; 0; 0; 0; 0; 0; 0; 0; 0; 0} | %
sludgefQ[] | Fraction of sludge flow from the layers | {0; 0; 0; 0; 0; 0; 0; 0; 0; 100} | %
Setpoints
Symbol | Name | Value | Unit | Comment
GCO2[] | Carbon dioxide gas (CO2) setpoint | {0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1} | g TIC/m3
GCH4[] | Methane gas (CH4) setpoint | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g COD/m3
GH2[] | Hydrogen gas (H2) setpoint | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g COD/m3
GO2[] | Oxygen gas (O2) setpoint | {1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32} | g O2/m3
GNH3[] | Ammonia gas (NH3) setpoint | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g N/m3
GN2[] | Nitrogen gas (N2) setpoint | {4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88} | g N/m3
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0[] | Volatile fatty acids (VFA) initial concentration | {0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01} | g COD/m3
SB_0[] | Readily biodegradable substrate (non-VFA) initial concentration | {1; 1; 1; 1; 1; 1; 1; 1; 1; 1} | g COD/m3
SMEOL_0[] | Methanol (MEOL) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g COD/m3
CB_0[] | Colloidal biodegradable substrate initial concentration | {0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01} | g COD/m3
XB_0[] | Slowly biodegradable substrate initial concentration | {5.6; 5.6; 5.6; 5.6; 5.6; 5.6; 5.6; 5.6; 5.6; 5.6} | g COD/m3
SU_0[] | Soluble unbiodegradable organics initial concentration | {7; 7; 7; 7; 7; 7; 7; 7; 7; 7} | g COD/m3
CU_0[] | Colloidal unbiodegradable organics initial concentration | {0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01} | g COD/m3
XU_0[] | Particulate unbiodegradable organics initial concentration | {400; 400; 400; 400; 400; 400; 400; 400; 400; 400} | g COD/m3
XPHA_0[] | Stored polyhydroxyalkanoates (PHA) initial concentration | {88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8} | g COD/m3
XGLY_0[] | Stored glycogen (GLY) initial concentration | {12; 12; 12; 12; 12; 12; 12; 12; 12; 12} | g COD/m3
XE_0[] | Endogenous decay products initial concentration | {120; 120; 120; 120; 120; 120; 120; 120; 120; 120} | g COD/m3
XE,ana_0[] | Anaerobic endogenous decay products initial concentration | {0.04; 0.04; 0.04; 0.04; 0.04; 0.04; 0.04; 0.04; 0.04; 0.04} | g COD/m3
XOHO_0[] | Ordinary heterotrophic organisms (OHO) initial concentration | {200; 200; 200; 200; 200; 200; 200; 200; 200; 200} | g COD/m3
XPAO_0[] | Phosphorus accumulating organisms (PAO) initial concentration | {148; 148; 148; 148; 148; 148; 148; 148; 148; 148} | g COD/m3
XGAO_0[] | Glycogen accumulating organisms (GAO) initial concentration | {148; 148; 148; 148; 148; 148; 148; 148; 148; 148} | g COD/m3
XMEOLO_0[] | Anoxic methanol utilizers (MEOLO) initial concentration | {0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4} | g COD/m3
XNITO_0[] | Aerobic nitrifying organisms (NITO) initial concentration | {36; 36; 36; 36; 36; 36; 36; 36; 36; 36} | g COD/m3
XAMETO_0[] | Acidoclastic methanogens (AMETO) initial concentration | {0.12; 0.12; 0.12; 0.12; 0.12; 0.12; 0.12; 0.12; 0.12; 0.12} | g COD/m3
XHMETO_0[] | Hydrogenotrophic methanogens (HMETO) initial concentration | {0.08; 0.08; 0.08; 0.08; 0.08; 0.08; 0.08; 0.08; 0.08; 0.08} | g COD/m3
SNHx_0[] | Total ammonia (NHx) initial concentration | {1; 1; 1; 1; 1; 1; 1; 1; 1; 1} | g N/m3
SNOx_0[] | Nitrate and nitrite (NOx) initial concentration | {5; 5; 5; 5; 5; 5; 5; 5; 5; 5} | g N/m3
SN2_0[] | Dissolved nitrogen (N2) initial concentration | {18; 18; 18; 18; 18; 18; 18; 18; 18; 18} | g N/m3
SN,B_0[] | Soluble biodegradable organic N (from SB) initial concentration | {0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5} | g N/m3
XN,B_0[] | Particulate biodegradable organic N (from XB) initial concentration | {0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4; 0.4} | g N/m3
XN,U_0[] | Particulate unbiodegradable organic N initial concentration | {4; 4; 4; 4; 4; 4; 4; 4; 4; 4} | g N/m3
SPO4_0[] | Orthophosphate (PO4) initial concentration | {0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5; 0.5} | g P/m3
XPP_0[] | Stored polyphosphate (PP) initial concentration | {88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8; 88.8} | g P/m3
SP,B_0[] | Soluble biodegradable organic P (from SB) initial concentration | {0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01} | g P/m3
XP,B_0[] | Particulate biodegradable organic P (from XB) initial concentration | {0.2; 0.2; 0.2; 0.2; 0.2; 0.2; 0.2; 0.2; 0.2; 0.2} | g P/m3
XP,U_0[] | Particulate unbiodegradable organic P initial concentration | {0.8; 0.8; 0.8; 0.8; 0.8; 0.8; 0.8; 0.8; 0.8; 0.8} | g P/m3
SO2_0[] | Dissolved oxygen (O2) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g O2/m3
SCH4_0[] | Dissolved methane (CH4) initial concentration | {0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01} | g COD/m3
SH2_0[] | Dissolved hydrogen (H2) initial concentration | {0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01; 0.01} | g COD/m3
SCO2_0[] | Total inorganic carbon (CO2) initial concentration | {74; 74; 74; 74; 74; 74; 74; 74; 74; 74} | g TIC/m3
XINORG_0[] | Inorganics in influent and biomass initial concentration | {184; 184; 184; 184; 184; 184; 184; 184; 184; 184} | g TSS/m3
SCAT_0[] | Other strong cations (as Na+) initial concentration | {35; 35; 35; 35; 35; 35; 35; 35; 35; 35} | g Na/m3
SAN_0[] | Other strong anions (as Cl-) initial concentration | {150; 150; 150; 150; 150; 150; 150; 150; 150; 150} | g Cl/m3
SCa_0[] | Calcium initial concentration | {150; 150; 150; 150; 150; 150; 150; 150; 150; 150} | g Ca/m3
SMg_0[] | Magnesium initial concentration | {15; 15; 15; 15; 15; 15; 15; 15; 15; 15} | g Mg/m3
SK_0[] | Potassium initial concentration | {15; 15; 15; 15; 15; 15; 15; 15; 15; 15} | g K/m3
SFe2_0[] | Ferrous ion (Fe2) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,H_0[] | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,L_0[] | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,old_0[] | Aged unused hydrous ferric oxide (HFO,old) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,H,P_0[] | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,L,P_0[] | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,H,P,old_0[] | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XHFO,L,P,old_0[] | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Fe/m3
XAlOH_0[] | Aluminium hydroxide compounds (AlOH) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Al/m3
XAlP_0[] | Aluminium phosphate compounds (AlP) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g Al/m3
XCaCO3_0[] | Calcium carbonate (CaCO3) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g TSS/m3
XACP_0[] | Amorphous calcium phosphate (ACP) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g TSS/m3
XSTR_0[] | Struvite (STR) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g TSS/m3
XVivi_0[] | Vivianite (Vivi) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g TSS/m3
H_0[] | Enthalpy initial concentration | {83626; 83626; 83626; 83626; 83626; 83626; 83626; 83626; 83626; 83626} | kJ.m-3
GCO2_0[] | Carbon dioxide gas (CO2) initial concentration | {0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1; 0.1} | g TIC/m3
GCH4_0[] | Methane gas (CH4) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g COD/m3
GH2_0[] | Hydrogen gas (H2) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g COD/m3
GO2_0[] | Oxygen gas (O2) initial concentration | {1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32; 1.32} | g O2/m3
GNH3_0[] | Ammonia gas (NH3) initial concentration | {1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40; 1E-40} | g N/m3
GN2_0[] | Nitrogen gas (N2) initial concentration | {4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88; 4.88} | g N/m3
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process | Flocculation factor | 0.75 |  | Only relevant for Sumo2C model

## Side flow combiner
Unit overview
Name: | Side flow combiner
Sumo name: | Sideflowcombiner1
Category: | Flow - energy elements
Unit: | Side flow combiner
Type: | Simple side flow combiner
Settings

## Side flow combiner2
Unit overview
Name: | Side flow combiner2
Sumo name: | Sideflowcombiner1_1
Category: | Flow - energy elements
Unit: | Side flow combiner
Type: | Simple side flow combiner
Settings

## External
Unit overview
Name: | External
Sumo name: | Sideflowdivider1
Category: | Flow - energy elements
Unit: | Side flow divider
Type: | Side pump
Settings
Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 385 | m3/d

## Internal
Unit overview
Name: | Internal
Sumo name: | Sideflowdivider2
Category: | Flow - energy elements
Unit: | Side flow divider
Type: | Side pump
Settings
Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 55338 | m3/d

## Effluent
Unit overview
Name: | Effluent
Sumo name: | Effluent1
Category: | Flow - energy elements
Unit: | Effluent
Type: | Plant effluent
Settings

## Sludge
Unit overview
Name: | Sludge
Sumo name: | Sludge1
Category: | Flow - energy elements
Unit: | Sludge
Type: | Sludge output
Settings